## English
Heat Exchanger Analysis (Effectiveness - NTU Method)
CheGuide.com |  |  | Tag No. | E-102 |  |  | 1 | Double Pipe - Parallel Flow |  |  |  | 5
Chemical Engineer's Guide |  |  | Description | Product Cooler |  |  | 2 | Double Pipe - Counter Flow
|  |  | Date | 27-Dec-15 |  |  | 3 | Shell & Tube - 1 Shell - 2,4, .. Tube Passes
User Input |  |  | By | CheGuide |  |  | 4 | Shell & Tube - 2 Shell - 4,8,.. Tube Passes
[7 empty] | 5 | Cross Flow - Both Fluid Unmixed
Fluid Data |  | Hot | Cold |  |  |  | 6 | Cross Flow - Lower Capacity Fluid Mixed
Flowrate | lb/h | 5000 | 6000 |  |  |  | 7 | Cross Flow - Higher Capacity Fluid Mixed
Inlet Temperature | °F | 150 | 60 |  |  |  | 8 | Cross Flow - Both Fluid Mixed
Specific Heat | BTU/lb.°F | 0.42 | 0.52
[9 empty] | Hot | Cold
Exchanger Data | [5 empty] | Flowrate |  |  | 5000 | 6000 |  | Heat Rate | 138499.4743 | BTU/h
Heat Exchanger Type |  | Cross Flow - Both Fluid Unmixed |  |  |  | Inlet Temperature |  |  | 150 | 60 |  | MTD | 27.6999 | oF
Heat Transfer Coefficient | BTU/h.ft².°F | 50 |  |  |  | Outlet Temperature |  |  | 84.0479 | 104.3909 |  | DT1 | 45.6091
Area | ft² | 100 |  |  |  | Specific Heat |  |  | 0.42 | 0.52 |  | DT2 | 24.0479
[6 empty] | Heat Transfer Coefficient |  |  | 50 |  |  | LMTD | 33.6862 | oF
Calculations | [5 empty] | Area |  |  | 100 |  |  | F | 0.82229
Heat Transfer Conductance | BTU/h.°F | 5000 |  |  |  | Conductance |  |  | 5000
Heat Transfer Rate | BTU/h | 138499.4743 |  |  |  | NTU |  |  | 2.381
Number of Transfer Units |  | 2.381 |  |  |  | Qmax |  |  | 189000 | BTU/h
Heat Capacity Ratio |  | 0.67308 |  |  |  | C_Hot | 2100 |  | C_Min | 2100 |  | Cr | 0.67308
Heat Exchanger Effectiveness |  | 0.7328 |  |  |  | C_Cold | 3120 |  | C_Max | 3120 |  | Epsilon | 0.7328
|  | Hot | Cold
Outlet Temperature | °F | 84.0479 | 104.3909
Flowrate * Specific Heat | BTU/h.°F | 2100 | 3120 |  |  | Drawing Case | [6 empty] | Line 1 | Xaxis | Yaxis
Mean temperature Difference | °F | 27.6999 | [11 empty] | 2.381 | 0
LMTD | °F | 33.6862 |  |  |  | NTU | 0.67308 | 0 | 0.4 | 0.8 | 1 |  |  | 2.381 | 1
[6 empty] | 0.0001 | 9.9969e-05 | 9.9995e-05 | 9.998e-05 | 9.9965e-05 | 9.9957e-05
[6 empty] | 0.01 | 0.009859 | 0.0099502 | 0.0098958 | 0.0098419 | 0.0098151 |  | Line 2 | Xaxis | Yaxis
[6 empty] | 0.02 | 0.019493 | 0.019801 | 0.019617 | 0.019435 | 0.019345 |  |  | 0 | 0.7328
[6 empty] | 0.03 | 0.028928 | 0.029554 | 0.02918 | 0.028811 | 0.02863 |  |  | 6 | 0.7328
[6 empty] | 0.04 | 0.038179 | 0.039211 | 0.038593 | 0.037988 | 0.03769
[6 empty] | 0.05 | 0.047255 | 0.048771 | 0.047863 | 0.046977 | 0.046542
[6 empty] | 0.06 | 0.056166 | 0.058235 | 0.056994 | 0.055787 | 0.055196
[6 empty] | 0.07 | 0.064919 | 0.067606 | 0.065992 | 0.064428 | 0.063664
[6 empty] | 0.08 | 0.073518 | 0.076884 | 0.07486 | 0.072905 | 0.071953
[6 empty] | 0.09 | 0.08197 | 0.086069 | 0.083601 | 0.081225 | 0.080071
[6 empty] | 0.1 | 0.090279 | 0.095163 | 0.09222 | 0.089395 | 0.088025
[6 empty] | 0.2 | 0.16639 | 0.18127 | 0.17223 | 0.16376 | 0.15973
[6 empty] | 0.4 | 0.2888 | 0.32968 | 0.30461 | 0.28179 | 0.27117
[6 empty] | 0.6 | 0.38291 | 0.45119 | 0.40915 | 0.37138 | 0.35404
[6 empty] | 0.8 | 0.4572 | 0.55067 | 0.4931 | 0.44148 | 0.41793
[6 empty] | 1 | 0.51703 | 0.63212 | 0.56141 | 0.49759 | 0.46854
[6 empty] | 1.5 | 0.6244 | 0.77687 | 0.68475 | 0.59773 | 0.55782
[6 empty] | 2 | 0.69446 | 0.86466 | 0.76466 | 0.66288 | 0.61541
[6 empty] | 2.5 | 0.74288 | 0.91792 | 0.81875 | 0.70801 | 0.65522
[6 empty] | 3 | 0.77786 | 0.95021 | 0.85671 | 0.74076 | 0.68421
[6 empty] | 3.5 | 0.80404 | 0.9698 | 0.88415 | 0.76545 | 0.70621
[6 empty] | 4 | 0.82422 | 0.98168 | 0.90451 | 0.78464 | 0.72349
[6 empty] | 4.5 | 0.84016 | 0.98889 | 0.91996 | 0.79995 | 0.73744
[6 empty] | 5 | 0.85302 | 0.99326 | 0.93191 | 0.81242 | 0.74898
[6 empty] | 5.5 | 0.86358 | 0.99591 | 0.94132 | 0.82279 | 0.75873
[6 empty] | 6 | 0.8724 | 0.99752 | 0.94884 | 0.83155 | 0.76712
Calculation Phase
[5 empty] | 1 | Double Pipe - Parallel Flow | [6 empty] | Solution |  |  | 3 | 1 Shell, 2,4 Tube Passes | [5 empty] | Solution
[18 empty] | 1.2054 | 1 | 1.077 | 1.2806 | 1.4142
[7 empty] | 0.67308 | 0 | 0.4 | 0.8 | 1 |  | NTU | 2.381 |  |  |  | 0.67308 | 0 | 0.4 | 0.8 | 1 | NTU | 2.381
[6 empty] | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05 |  | Epsilon | 0.58657 |  |  | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05 | Epsilon | 0.66151
[6 empty] | 0.01 | 0.0099168 | 0.0099502 | 0.0099303 | 0.0099105 | 0.0099007 | [5 empty] | 0.01 | 0.0099169 | 0.0099502 | 0.0099304 | 0.0099107 | 0.0099008
[6 empty] | 0.02 | 0.019669 | 0.019801 | 0.019723 | 0.019644 | 0.019605 | [5 empty] | 0.02 | 0.01967 | 0.019801 | 0.019723 | 0.019645 | 0.019607
[6 empty] | 0.03 | 0.02926 | 0.029554 | 0.029379 | 0.029204 | 0.029118 | [5 empty] | 0.03 | 0.029262 | 0.029554 | 0.02938 | 0.029208 | 0.029122
[6 empty] | 0.04 | 0.038691 | 0.039211 | 0.038901 | 0.038594 | 0.038442 | [5 empty] | 0.04 | 0.038698 | 0.039211 | 0.038905 | 0.038602 | 0.038452
[6 empty] | 0.05 | 0.047966 | 0.048771 | 0.04829 | 0.047816 | 0.047581 | [5 empty] | 0.05 | 0.047979 | 0.048771 | 0.048298 | 0.047831 | 0.0476
[6 empty] | 0.06 | 0.057087 | 0.058235 | 0.057549 | 0.056874 | 0.05654 | [5 empty] | 0.06 | 0.057109 | 0.058235 | 0.057562 | 0.056899 | 0.056572
[6 empty] | 0.07 | 0.066056 | 0.067606 | 0.066679 | 0.06577 | 0.065321 | [5 empty] | 0.07 | 0.066091 | 0.067606 | 0.0667 | 0.06581 | 0.065371
[6 empty] | 0.08 | 0.074877 | 0.076884 | 0.075683 | 0.074507 | 0.073928 | [5 empty] | 0.08 | 0.074928 | 0.076884 | 0.075713 | 0.074566 | 0.074001
[6 empty] | 0.09 | 0.083552 | 0.086069 | 0.084561 | 0.083088 | 0.082365 | [5 empty] | 0.09 | 0.083622 | 0.086069 | 0.084604 | 0.083171 | 0.082467
[6 empty] | 0.1 | 0.092082 | 0.095163 | 0.093316 | 0.091517 | 0.090635 | [5 empty] | 0.1 | 0.092177 | 0.095163 | 0.093374 | 0.091628 | 0.090772
[6 empty] | 0.2 | 0.16998 | 0.18127 | 0.17444 | 0.16796 | 0.16484 | [5 empty] | 0.2 | 0.17063 | 0.18127 | 0.17485 | 0.16871 | 0.16575
[6 empty] | 0.4 | 0.29162 | 0.32968 | 0.30628 | 0.28514 | 0.27534 | [5 empty] | 0.4 | 0.29544 | 0.32968 | 0.30878 | 0.28948 | 0.2804
[6 empty] | 0.6 | 0.37866 | 0.45119 | 0.40592 | 0.36689 | 0.3494 | [5 empty] | 0.6 | 0.38831 | 0.45119 | 0.4125 | 0.37766 | 0.3616
[6 empty] | 0.8 | 0.44095 | 0.55067 | 0.48123 | 0.42393 | 0.39905 | [5 empty] | 0.8 | 0.45831 | 0.55067 | 0.49349 | 0.44297 | 0.42007
[6 empty] | 1 | 0.48553 | 0.63212 | 0.53815 | 0.46372 | 0.43233 | [5 empty] | 1 | 0.51156 | 0.63212 | 0.55715 | 0.49187 | 0.46267
[6 empty] | 1.5 | 0.54911 | 0.77687 | 0.62682 | 0.51822 | 0.47511 | [5 empty] | 1.5 | 0.59678 | 0.77687 | 0.66413 | 0.56816 | 0.52639
[6 empty] | 2 | 0.57665 | 0.86466 | 0.67085 | 0.54038 | 0.49084 | [5 empty] | 2 | 0.64181 | 0.86466 | 0.72471 | 0.607 | 0.55681
[6 empty] | 2.5 | 0.58858 | 0.91792 | 0.69272 | 0.54938 | 0.49663 | [5 empty] | 2.5 | 0.666 | 0.91792 | 0.75946 | 0.6271 | 0.57157
[6 empty] | 3 | 0.59375 | 0.95021 | 0.70357 | 0.55305 | 0.49876 | [5 empty] | 3 | 0.67909 | 0.95021 | 0.77953 | 0.6376 | 0.5788
[6 empty] | 3.5 | 0.59599 | 0.9698 | 0.70897 | 0.55454 | 0.49954 | [5 empty] | 3.5 | 0.68622 | 0.9698 | 0.79118 | 0.6431 | 0.58234
[6 empty] | 4 | 0.59696 | 0.98168 | 0.71164 | 0.55514 | 0.49983 | [5 empty] | 4 | 0.69011 | 0.98168 | 0.79795 | 0.646 | 0.58409
[6 empty] | 4.5 | 0.59738 | 0.98889 | 0.71297 | 0.55539 | 0.49994 | [5 empty] | 4.5 | 0.69224 | 0.98889 | 0.8019 | 0.64752 | 0.58495
[6 empty] | 5 | 0.59756 | 0.99326 | 0.71363 | 0.55549 | 0.49998 | [5 empty] | 5 | 0.6934 | 0.99326 | 0.8042 | 0.64832 | 0.58537
[6 empty] | 5.5 | 0.59764 | 0.99591 | 0.71396 | 0.55553 | 0.49999 | [5 empty] | 5.5 | 0.69404 | 0.99591 | 0.80554 | 0.64875 | 0.58558
[6 empty] | 6 | 0.59768 | 0.99752 | 0.71413 | 0.55554 | 0.5 | [5 empty] | 6 | 0.69439 | 0.99752 | 0.80632 | 0.64897 | 0.58569
[5 empty] | 2 | Double Pipe - Counter Flow | [6 empty] | Solution |  |  | 4 | 2 Shell, 4,8 Tube Passes | [5 empty] | Solution
[27 empty] | 1.2054 | 1 | 1.077 | 1.2806 | 1.4142
[7 empty] | 0.67308 | 0 | 0.4 | 0.8 | 1 |  | NTU | 2.381 |  |  |  | 0.67308 | 0 | 0.4 | 0.8 | 1 | NTU | 2.381 |  |  | 0.67308 | 0 | 0.4 | 0.8 | 1
[6 empty] | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05 |  | Epsilon | 0.78276 |  |  | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.991e-05 | Epsilon | 0.74633 |  | 5e-05 | 4.9998e-05 | 4.9999e-05 | 4.9998e-05 | 4.9998e-05 | 4.9998e-05
[6 empty] | 0.01 | 0.009917 | 0.0099502 | 0.0099305 | 0.0099108 | 0.009901 | [5 empty] | 0.01 | 0.009917 | 0.0099502 | 0.0099304 | 0.0099108 | 0.009901 |  |  |  | 0.005 | 0.0049792 | 0.0049875 | 0.0049825 | 0.0049776 | 0.0049751
[6 empty] | 0.02 | 0.019671 | 0.019801 | 0.019724 | 0.019646 | 0.019608 | [5 empty] | 0.02 | 0.019671 | 0.019801 | 0.019724 | 0.019646 | 0.019607 |  |  |  | 0.01 | 0.0099169 | 0.0099502 | 0.0099304 | 0.0099107 | 0.0099008
[6 empty] | 0.03 | 0.029265 | 0.029554 | 0.029382 | 0.029211 | 0.029126 | [5 empty] | 0.03 | 0.029265 | 0.029554 | 0.029382 | 0.02921 | 0.029125 |  |  |  | 0.015 | 0.014814 | 0.014888 | 0.014844 | 0.0148 | 0.014778
[6 empty] | 0.04 | 0.038704 | 0.039211 | 0.038909 | 0.03861 | 0.038462 | [5 empty] | 0.04 | 0.038703 | 0.039211 | 0.038908 | 0.038608 | 0.038459 |  |  |  | 0.02 | 0.01967 | 0.019801 | 0.019723 | 0.019645 | 0.019607
[6 empty] | 0.05 | 0.047992 | 0.048771 | 0.048306 | 0.047847 | 0.047619 | [5 empty] | 0.05 | 0.047988 | 0.048771 | 0.048304 | 0.047843 | 0.047614 |  |  |  | 0.025 | 0.024486 | 0.02469 | 0.024569 | 0.024448 | 0.024388
[6 empty] | 0.06 | 0.057131 | 0.058235 | 0.057576 | 0.056925 | 0.056604 | [5 empty] | 0.06 | 0.057125 | 0.058235 | 0.057572 | 0.056919 | 0.056596 |  |  |  | 0.03 | 0.029262 | 0.029554 | 0.02938 | 0.029208 | 0.029122 | NTU
[6 empty] | 0.07 | 0.066125 | 0.067606 | 0.066721 | 0.06585 | 0.065421 | [5 empty] | 0.07 | 0.066116 | 0.067606 | 0.066716 | 0.06584 | 0.065408 |  |  |  | 0.035 | 0.033999 | 0.034395 | 0.034159 | 0.033926 | 0.03381 | Epsilon
[6 empty] | 0.08 | 0.074978 | 0.076884 | 0.075744 | 0.074625 | 0.074074 | [5 empty] | 0.08 | 0.074965 | 0.076884 | 0.075736 | 0.074611 | 0.074056 |  |  |  | 0.04 | 0.038698 | 0.039211 | 0.038905 | 0.038602 | 0.038452
[6 empty] | 0.09 | 0.083693 | 0.086069 | 0.084647 | 0.083254 | 0.082569 | [5 empty] | 0.09 | 0.083675 | 0.086069 | 0.084636 | 0.083233 | 0.082543 |  |  |  | 0.045 | 0.043357 | 0.044003 | 0.043618 | 0.043237 | 0.043048
[6 empty] | 0.1 | 0.092273 | 0.095163 | 0.093432 | 0.09174 | 0.090909 | [5 empty] | 0.1 | 0.092249 | 0.095163 | 0.093417 | 0.091712 | 0.090875 |  |  |  | 0.05 | 0.047979 | 0.048771 | 0.048298 | 0.047831 | 0.0476
[6 empty] | 0.2 | 0.17128 | 0.18127 | 0.17525 | 0.16947 | 0.16667 | [5 empty] | 0.2 | 0.17112 | 0.18127 | 0.17515 | 0.16928 | 0.16644 |  |  |  | 0.1 | 0.092177 | 0.095163 | 0.093374 | 0.091628 | 0.090772
[6 empty] | 0.4 | 0.29939 | 0.32968 | 0.31133 | 0.294 | 0.28571 | [5 empty] | 0.4 | 0.29839 | 0.32968 | 0.31069 | 0.29286 | 0.28436 |  |  |  | 0.2 | 0.17063 | 0.18127 | 0.17485 | 0.16871 | 0.16575
[6 empty] | 0.6 | 0.39864 | 0.45119 | 0.41935 | 0.38931 | 0.375 | [5 empty] | 0.6 | 0.39599 | 0.45119 | 0.41762 | 0.38631 | 0.37153 |  |  |  | 0.3 | 0.23775 | 0.25918 | 0.24617 | 0.23396 | 0.22814
[6 empty] | 0.8 | 0.47763 | 0.55067 | 0.50661 | 0.46454 | 0.44444 | [5 empty] | 0.8 | 0.47261 | 0.55067 | 0.50327 | 0.45889 | 0.43799 |  |  |  | 0.4 | 0.29544 | 0.32968 | 0.30878 | 0.28948 | 0.2804
[6 empty] | 1 | 0.54188 | 0.63212 | 0.57809 | 0.52539 | 0.5 | [5 empty] | 1 | 0.53387 | 0.63212 | 0.57273 | 0.51643 | 0.48988 |  |  |  | 0.5 | 0.34522 | 0.39347 | 0.36389 | 0.33694 | 0.3244
[6 empty] | 1.5 | 0.65941 | 0.77687 | 0.70868 | 0.63627 | 0.6 | [5 empty] | 1.5 | 0.6421 | 0.77687 | 0.69708 | 0.61704 | 0.5787 |  |  |  | 0.75 | 0.44258 | 0.52763 | 0.47505 | 0.4284 | 0.40716 |  | 1.1905
[6 empty] | 2 | 0.73843 | 0.86466 | 0.79453 | 0.71091 | 0.66667 | [5 empty] | 2 | 0.71042 | 0.86466 | 0.77608 | 0.67983 | 0.63264 |  |  |  | 1 | 0.51156 | 0.63212 | 0.55715 | 0.49187 | 0.46267 |  | 0.55067
[6 empty] | 2.5 | 0.79456 | 0.91792 | 0.853 | 0.76435 | 0.71429 | [5 empty] | 2.5 | 0.7555 | 0.91792 | 0.82801 | 0.72089 | 0.66706 |  |  |  | 1.25 | 0.56102 | 0.7135 | 0.6183 | 0.53649 | 0.50044
[6 empty] | 3 | 0.836 | 0.95021 | 0.8938 | 0.80433 | 0.75 | [5 empty] | 3 | 0.78615 | 0.95021 | 0.86303 | 0.74859 | 0.68972 |  |  |  | 1.5 | 0.59678 | 0.77687 | 0.66413 | 0.56816 | 0.52639
[6 empty] | 3.5 | 0.86748 | 0.9698 | 0.92274 | 0.83522 | 0.77778 | [5 empty] | 3.5 | 0.80745 | 0.9698 | 0.88715 | 0.76766 | 0.70495 |  |  |  | 1.75 | 0.6228 | 0.82623 | 0.69864 | 0.59077 | 0.54434
[6 empty] | 4 | 0.89191 | 0.98168 | 0.94352 | 0.8597 | 0.8 | [5 empty] | 4 | 0.82248 | 0.98168 | 0.90406 | 0.78099 | 0.71532 |  |  |  | 2 | 0.64181 | 0.86466 | 0.72471 | 0.607 | 0.55681
[6 empty] | 4.5 | 0.91119 | 0.98889 | 0.95856 | 0.87949 | 0.81818 | [5 empty] | 4.5 | 0.83322 | 0.98889 | 0.9161 | 0.79041 | 0.72245 |  |  |  | 2.25 | 0.65575 | 0.8946 | 0.74446 | 0.61867 | 0.5655
[6 empty] | 5 | 0.92661 | 0.99326 | 0.96952 | 0.89574 | 0.83333 | [5 empty] | 5 | 0.84096 | 0.99326 | 0.92479 | 0.79712 | 0.72739 |  |  |  | 2.5 | 0.666 | 0.91792 | 0.75946 | 0.6271 | 0.57157
[6 empty] | 5.5 | 0.93906 | 0.99591 | 0.97754 | 0.90926 | 0.84615 | [5 empty] | 5.5 | 0.84657 | 0.99591 | 0.93112 | 0.80192 | 0.73082 |  |  |  | 2.75 | 0.67354 | 0.93607 | 0.77085 | 0.63319 | 0.57582
[6 empty] | 6 | 0.94921 | 0.99752 | 0.98342 | 0.92064 | 0.85714 | [5 empty] | 6 | 0.85067 | 0.99752 | 0.93578 | 0.80536 | 0.73321 |  |  |  | 3 | 0.67909 | 0.95021 | 0.77953 | 0.6376 | 0.5788
[5 empty] | 5 | Cross Flow - Both Pass Unmixed | [6 empty] | Solution |  |  | 6 | Cross Flow - Lower Capacity Fluid Mixed | [5 empty] | Solution |  | 7 | Cross Flow - Higher Capacity Fluid Mixed
[7 empty] | 0.67308 | 0 | 0.4 | 0.8 | 1 |  | NTU | 2.381 |  |  |  | 0.67308 | 0 | 0.4 | 0.8 | 1 | NTU | 2.381 |  |  | 0.67308 | 0 | 0.4 | 0.8 | 1
[6 empty] | 0.0001 | 9.9969e-05 | 9.9995e-05 | 9.998e-05 | 9.9965e-05 | 9.9957e-05 |  | Epsilon | 0.7328 |  |  | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05 | Epsilon | 0.69472 |  | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05
[6 empty] | 0.01 | 0.009859 | 0.0099502 | 0.0098958 | 0.0098419 | 0.0098151 | [5 empty] | 0.01 | 0.0099169 | 0.0099502 | 0.0099304 | 0.0099107 | 0.0099008 |  |  |  | 0.01 | 0.0099169 | 0.0099502 | 0.0099304 | 0.0099107 | 0.0099008
[6 empty] | 0.02 | 0.019493 | 0.019801 | 0.019617 | 0.019435 | 0.019345 | [5 empty] | 0.02 | 0.01967 | 0.019801 | 0.019723 | 0.019645 | 0.019607 |  |  |  | 0.02 | 0.01967 | 0.019801 | 0.019723 | 0.019645 | 0.019607
[6 empty] | 0.03 | 0.028928 | 0.029554 | 0.02918 | 0.028811 | 0.02863 | [5 empty] | 0.03 | 0.029262 | 0.029554 | 0.02938 | 0.029208 | 0.029122 |  |  |  | 0.03 | 0.029262 | 0.029554 | 0.02938 | 0.029208 | 0.029122
[6 empty] | 0.04 | 0.038179 | 0.039211 | 0.038593 | 0.037988 | 0.03769 | [5 empty] | 0.04 | 0.038698 | 0.039211 | 0.038905 | 0.038602 | 0.038452 |  |  |  | 0.04 | 0.038698 | 0.039211 | 0.038905 | 0.038602 | 0.038452 | Solution
[6 empty] | 0.05 | 0.047255 | 0.048771 | 0.047863 | 0.046977 | 0.046542 | [5 empty] | 0.05 | 0.047979 | 0.048771 | 0.048298 | 0.047831 | 0.0476 |  |  |  | 0.05 | 0.047979 | 0.048771 | 0.048298 | 0.047831 | 0.0476
[6 empty] | 0.06 | 0.056166 | 0.058235 | 0.056994 | 0.055787 | 0.055196 | [5 empty] | 0.06 | 0.057109 | 0.058235 | 0.057563 | 0.0569 | 0.056572 |  |  |  | 0.06 | 0.057109 | 0.058235 | 0.057562 | 0.0569 | 0.056572 | NTU
[6 empty] | 0.07 | 0.064919 | 0.067606 | 0.065992 | 0.064428 | 0.063664 | [5 empty] | 0.07 | 0.066091 | 0.067606 | 0.0667 | 0.065811 | 0.065372 |  |  |  | 0.07 | 0.066091 | 0.067606 | 0.0667 | 0.06581 | 0.065372 | Epsilon
[6 empty] | 0.08 | 0.073518 | 0.076884 | 0.07486 | 0.072905 | 0.071953 | [5 empty] | 0.08 | 0.074929 | 0.076884 | 0.075714 | 0.074567 | 0.074002 |  |  |  | 0.08 | 0.074928 | 0.076884 | 0.075713 | 0.074567 | 0.074002
[6 empty] | 0.09 | 0.08197 | 0.086069 | 0.083601 | 0.081225 | 0.080071 | [5 empty] | 0.09 | 0.083624 | 0.086069 | 0.084605 | 0.083173 | 0.082469 |  |  |  | 0.09 | 0.083623 | 0.086069 | 0.084604 | 0.083173 | 0.082469
[6 empty] | 0.1 | 0.090279 | 0.095163 | 0.09222 | 0.089395 | 0.088025 | [5 empty] | 0.1 | 0.09218 | 0.095163 | 0.093375 | 0.091631 | 0.090775 |  |  |  | 0.1 | 0.092179 | 0.095163 | 0.093374 | 0.09163 | 0.090775
[6 empty] | 0.2 | 0.16639 | 0.18127 | 0.17223 | 0.16376 | 0.15973 | [5 empty] | 0.2 | 0.17066 | 0.18127 | 0.17487 | 0.16875 | 0.16579 |  |  |  | 0.2 | 0.17065 | 0.18127 | 0.17485 | 0.16874 | 0.16579
[6 empty] | 0.4 | 0.2888 | 0.32968 | 0.30461 | 0.28179 | 0.27117 | [5 empty] | 0.4 | 0.29579 | 0.32968 | 0.30902 | 0.28987 | 0.28085 |  |  |  | 0.4 | 0.29566 | 0.32968 | 0.30887 | 0.28979 | 0.28085
[6 empty] | 0.6 | 0.38291 | 0.45119 | 0.40915 | 0.37138 | 0.35404 | [5 empty] | 0.6 | 0.3896 | 0.45119 | 0.41341 | 0.37906 | 0.36313 |  |  |  | 0.6 | 0.38912 | 0.45119 | 0.41282 | 0.37873 | 0.36313
[6 empty] | 0.8 | 0.4572 | 0.55067 | 0.4931 | 0.44148 | 0.41793 | [5 empty] | 0.8 | 0.46129 | 0.55067 | 0.49572 | 0.44616 | 0.42344 |  |  |  | 0.8 | 0.46014 | 0.55067 | 0.49424 | 0.44539 | 0.42344
[6 empty] | 1 | 0.51703 | 0.63212 | 0.56141 | 0.49759 | 0.46854 | [5 empty] | 1 | 0.51703 | 0.63212 | 0.56141 | 0.49759 | 0.46854 |  |  |  | 1 | 0.51485 | 0.63212 | 0.55854 | 0.49614 | 0.46854
[6 empty] | 1.5 | 0.6244 | 0.77687 | 0.68475 | 0.59773 | 0.55782 | [5 empty] | 1.5 | 0.61108 | 0.77687 | 0.67631 | 0.58252 | 0.54016 |  |  |  | 1.5 | 0.60498 | 0.77687 | 0.66775 | 0.57857 | 0.54016 |  | 2.381
[6 empty] | 2 | 0.69446 | 0.86466 | 0.76466 | 0.66288 | 0.61541 | [5 empty] | 2 | 0.66682 | 0.86466 | 0.74758 | 0.63125 | 0.57881 |  |  |  | 2 | 0.65552 | 0.86466 | 0.73098 | 0.62411 | 0.57881 |  | 0.67913
[6 empty] | 2.5 | 0.74288 | 0.91792 | 0.81875 | 0.70801 | 0.65522 | [5 empty] | 2.5 | 0.70167 | 0.91792 | 0.79409 | 0.66069 | 0.60065 |  |  |  | 2.5 | 0.68474 | 0.91792 | 0.76826 | 0.65022 | 0.60065
[6 empty] | 3 | 0.77786 | 0.95021 | 0.85671 | 0.74076 | 0.68421 | [5 empty] | 3 | 0.72431 | 0.95021 | 0.82571 | 0.67909 | 0.61334 |  |  |  | 3 | 0.70197 | 0.95021 | 0.79049 | 0.66552 | 0.61334
[6 empty] | 3.5 | 0.80404 | 0.9698 | 0.88415 | 0.76545 | 0.70621 | [5 empty] | 3.5 | 0.73942 | 0.9698 | 0.84794 | 0.69087 | 0.62084 |  |  |  | 3.5 | 0.71223 | 0.9698 | 0.80384 | 0.67461 | 0.62084
[6 empty] | 4 | 0.82422 | 0.98168 | 0.90451 | 0.78464 | 0.72349 | [5 empty] | 4 | 0.7497 | 0.98168 | 0.86402 | 0.69852 | 0.62532 |  |  |  | 4 | 0.7184 | 0.98168 | 0.81188 | 0.68005 | 0.62532
[6 empty] | 4.5 | 0.84016 | 0.98889 | 0.91996 | 0.79995 | 0.73744 | [5 empty] | 4.5 | 0.75679 | 0.98889 | 0.87591 | 0.70354 | 0.62801 |  |  |  | 4.5 | 0.72211 | 0.98889 | 0.81674 | 0.68332 | 0.62801
[6 empty] | 5 | 0.85302 | 0.99326 | 0.93191 | 0.81242 | 0.74898 | [5 empty] | 5 | 0.76174 | 0.99326 | 0.88487 | 0.70686 | 0.62963 |  |  |  | 5 | 0.72435 | 0.99326 | 0.81968 | 0.6853 | 0.62963
[6 empty] | 5.5 | 0.86358 | 0.99591 | 0.94132 | 0.82279 | 0.75873 | [5 empty] | 5.5 | 0.76521 | 0.99591 | 0.89172 | 0.70906 | 0.63061 |  |  |  | 5.5 | 0.72571 | 0.99591 | 0.82146 | 0.6865 | 0.63061
[6 empty] | 6 | 0.8724 | 0.99752 | 0.94884 | 0.83155 | 0.76712 | [5 empty] | 6 | 0.76765 | 0.99752 | 0.89702 | 0.71053 | 0.63121 |  |  |  | 6 | 0.72653 | 0.99752 | 0.82254 | 0.68722 | 0.63121
[5 empty] | 8 | Cross Flow - Both Pass Mixed | [6 empty] | Solution
[7 empty] | 0.67308 | 0 | 0.4 | 0.8 | 1 |  | NTU | 2.381
[6 empty] | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05 |  | Epsilon | 0.65587
[6 empty] | 0.01 | 0.0099169 | 0.0099502 | 0.0099304 | 0.0099107 | 0.0099008
[6 empty] | 0.02 | 0.01967 | 0.019801 | 0.019723 | 0.019645 | 0.019607
[6 empty] | 0.03 | 0.029262 | 0.029554 | 0.02938 | 0.029208 | 0.029122
[6 empty] | 0.04 | 0.038698 | 0.039211 | 0.038905 | 0.038602 | 0.038452
[6 empty] | 0.05 | 0.047979 | 0.048771 | 0.048298 | 0.047831 | 0.0476
[6 empty] | 0.06 | 0.057109 | 0.058235 | 0.057562 | 0.056899 | 0.056572
[6 empty] | 0.07 | 0.066091 | 0.067606 | 0.0667 | 0.06581 | 0.065371
[6 empty] | 0.08 | 0.074928 | 0.076884 | 0.075713 | 0.074566 | 0.074001
[6 empty] | 0.09 | 0.083622 | 0.086069 | 0.084604 | 0.083171 | 0.082467
[6 empty] | 0.1 | 0.092177 | 0.095163 | 0.093374 | 0.091628 | 0.090772
[6 empty] | 0.2 | 0.17063 | 0.18127 | 0.17485 | 0.16871 | 0.16575
[6 empty] | 0.4 | 0.29543 | 0.32968 | 0.30878 | 0.28947 | 0.28039
[6 empty] | 0.6 | 0.38827 | 0.45119 | 0.41248 | 0.37761 | 0.36152
[6 empty] | 0.8 | 0.45818 | 0.55067 | 0.49343 | 0.4428 | 0.41983
[6 empty] | 1 | 0.51125 | 0.63212 | 0.55702 | 0.49146 | 0.46212
[6 empty] | 1.5 | 0.59543 | 0.77687 | 0.66353 | 0.56646 | 0.52417
[6 empty] | 2 | 0.63842 | 0.86466 | 0.72312 | 0.60281 | 0.55156
[6 empty] | 2.5 | 0.65956 | 0.91792 | 0.75631 | 0.61933 | 0.56216
[6 empty] | 3 | 0.66882 | 0.95021 | 0.77431 | 0.62544 | 0.56451
[6 empty] | 3.5 | 0.67159 | 0.9698 | 0.78349 | 0.62609 | 0.56289
[6 empty] | 4 | 0.67086 | 0.98168 | 0.7875 | 0.62397 | 0.5595
[6 empty] | 4.5 | 0.66831 | 0.98889 | 0.7885 | 0.62055 | 0.55548
[6 empty] | 5 | 0.66492 | 0.99326 | 0.78778 | 0.61663 | 0.5514
[6 empty] | 5.5 | 0.6612 | 0.99591 | 0.78608 | 0.61266 | 0.54753
[6 empty] | 6 | 0.65747 | 0.99752 | 0.78387 | 0.60884 | 0.54398

## Metric
Heat Exchanger Analysis (Effectiveness - NTU Method)
CheGuide.com |  |  | Tag No. | E-102 |  |  | 1 | Double Pipe - Parallel Flow |  |  |  | 5
Chemical Engineer's Guide |  |  | Description | Product Cooler |  |  | 2 | Double Pipe - Counter Flow
|  |  | Date | 27-Dec-15 |  |  | 3 | Shell & Tube - 1 Shell - 2,4, .. Tube Passes
User Input |  |  | By | CheGuide |  |  | 4 | Shell & Tube - 2 Shell - 4,8,.. Tube Passes
[7 empty] | 5 | Cross Flow - Both Fluid Unmixed
Fluid Data |  | Hot | Cold |  |  |  | 6 | Cross Flow - Lower Capacity Fluid Mixed
Flowrate | kg/h | 2267.9619 | 2721.5542 |  |  |  | 7 | Cross Flow - Higher Capacity Fluid Mixed
Inlet Temperature | °C | 65.5556 | 15.5556 |  |  |  | 8 | Cross Flow - Both Fluid Mixed
Specific Heat | kcal/kg.°C | 0.42 | 0.52
[9 empty] | Hot | Cold
Exchanger Data | [5 empty] | Flowrate |  |  | 2267.9619 | 2721.5542 |  | Heat Rate | 34901.2804 | BTU/h
Heat Exchanger Type |  | Cross Flow - Both Fluid Unmixed |  |  |  | Inlet Temperature |  |  | 65.5556 | 15.5556 |  | MTD | 15.3888 | oF
Heat Transfer Coefficient | kcal/h.m².°C | 244.1214 |  |  |  | Outlet Temperature |  |  | 28.9155 | 40.2171 |  | DT1 | 25.3384
Area | m² | 9.2903 |  |  |  | Specific Heat |  |  | 0.42 | 0.52 |  | DT2 | 13.3599
[6 empty] | Heat Transfer Coefficient |  |  | 244.1214 |  |  | LMTD | 18.7146 | oF
Calculations | [5 empty] | Area |  |  | 9.2903 |  |  | F | 0.82229
Heat Transfer Conductance | kcal/h.°C | 2267.9618 |  |  |  | Conductance |  |  | 2267.9618
Heat Transfer Rate | kcal/h | 34901.2804 |  |  |  | NTU |  |  | 2.381
Number of Transfer Units |  | 2.381 |  |  |  | Qmax |  |  | 47627.1989 | BTU/h
Heat Capacity Ratio |  | 0.67308 |  |  |  | C_Hot | 952.544 |  | C_Min | 952.544 |  | Cr | 0.67308
Heat Exchanger Effectiveness |  | 0.7328 |  |  |  | C_Cold | 1415.2082 |  | C_Max | 1415.2082 |  | Epsilon | 0.7328
|  | Hot | Cold
Outlet Temperature | °C | 28.9155 | 40.2171
Flowrate * Specific Heat | kcal/h.°C | 952.544 | 1415.2082 |  |  | Drawing Case | [6 empty] | Line 1 | Xaxis | Yaxis
Mean temperature Difference | °C | 15.3888 | [11 empty] | 2.381 | 0
LMTD | °C | 18.7146 |  |  |  | NTU | 0.67308 | 0 | 0.4 | 0.8 | 1 |  |  | 2.381 | 1
[6 empty] | 0.0001 | 9.9969e-05 | 9.9995e-05 | 9.998e-05 | 9.9965e-05 | 9.9957e-05
[6 empty] | 0.01 | 0.009859 | 0.0099502 | 0.0098958 | 0.0098419 | 0.0098151 |  | Line 2 | Xaxis | Yaxis
[6 empty] | 0.02 | 0.019493 | 0.019801 | 0.019617 | 0.019435 | 0.019345 |  |  | 0 | 0.7328
[6 empty] | 0.03 | 0.028928 | 0.029554 | 0.02918 | 0.028811 | 0.02863 |  |  | 6 | 0.7328
[6 empty] | 0.04 | 0.038179 | 0.039211 | 0.038593 | 0.037988 | 0.03769
[6 empty] | 0.05 | 0.047255 | 0.048771 | 0.047863 | 0.046977 | 0.046542
[6 empty] | 0.06 | 0.056166 | 0.058235 | 0.056994 | 0.055787 | 0.055196
[6 empty] | 0.07 | 0.064919 | 0.067606 | 0.065992 | 0.064428 | 0.063664
[6 empty] | 0.08 | 0.073518 | 0.076884 | 0.07486 | 0.072905 | 0.071953
[6 empty] | 0.09 | 0.08197 | 0.086069 | 0.083601 | 0.081225 | 0.080071
[6 empty] | 0.1 | 0.090279 | 0.095163 | 0.09222 | 0.089395 | 0.088025
[6 empty] | 0.2 | 0.16639 | 0.18127 | 0.17223 | 0.16376 | 0.15973
[6 empty] | 0.4 | 0.2888 | 0.32968 | 0.30461 | 0.28179 | 0.27117
[6 empty] | 0.6 | 0.38291 | 0.45119 | 0.40915 | 0.37138 | 0.35404
[6 empty] | 0.8 | 0.4572 | 0.55067 | 0.4931 | 0.44148 | 0.41793
[6 empty] | 1 | 0.51703 | 0.63212 | 0.56141 | 0.49759 | 0.46854
[6 empty] | 1.5 | 0.6244 | 0.77687 | 0.68475 | 0.59773 | 0.55782
[6 empty] | 2 | 0.69446 | 0.86466 | 0.76466 | 0.66288 | 0.61541
[6 empty] | 2.5 | 0.74288 | 0.91792 | 0.81875 | 0.70801 | 0.65522
[6 empty] | 3 | 0.77786 | 0.95021 | 0.85671 | 0.74076 | 0.68421
[6 empty] | 3.5 | 0.80404 | 0.9698 | 0.88415 | 0.76545 | 0.70621
[6 empty] | 4 | 0.82422 | 0.98168 | 0.90451 | 0.78464 | 0.72349
[6 empty] | 4.5 | 0.84016 | 0.98889 | 0.91996 | 0.79995 | 0.73744
[6 empty] | 5 | 0.85302 | 0.99326 | 0.93191 | 0.81242 | 0.74898
[6 empty] | 5.5 | 0.86358 | 0.99591 | 0.94132 | 0.82279 | 0.75873
[6 empty] | 6 | 0.8724 | 0.99752 | 0.94884 | 0.83155 | 0.76712
Calculation Phase
[5 empty] | 1 | Double Pipe - Parallel Flow | [6 empty] | Solution |  |  | 3 | 1 Shell, 2,4 Tube Passes | [5 empty] | Solution
[18 empty] | 1.2054 | 1 | 1.077 | 1.2806 | 1.4142
[7 empty] | 0.67308 | 0 | 0.4 | 0.8 | 1 |  | NTU | 2.381 |  |  |  | 0.67308 | 0 | 0.4 | 0.8 | 1 | NTU | 2.381
[6 empty] | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05 |  | Epsilon | 0.58657 |  |  | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05 | Epsilon | 0.66151
[6 empty] | 0.01 | 0.0099168 | 0.0099502 | 0.0099303 | 0.0099105 | 0.0099007 | [5 empty] | 0.01 | 0.0099169 | 0.0099502 | 0.0099304 | 0.0099107 | 0.0099008
[6 empty] | 0.02 | 0.019669 | 0.019801 | 0.019723 | 0.019644 | 0.019605 | [5 empty] | 0.02 | 0.01967 | 0.019801 | 0.019723 | 0.019645 | 0.019607
[6 empty] | 0.03 | 0.02926 | 0.029554 | 0.029379 | 0.029204 | 0.029118 | [5 empty] | 0.03 | 0.029262 | 0.029554 | 0.02938 | 0.029208 | 0.029122
[6 empty] | 0.04 | 0.038691 | 0.039211 | 0.038901 | 0.038594 | 0.038442 | [5 empty] | 0.04 | 0.038698 | 0.039211 | 0.038905 | 0.038602 | 0.038452
[6 empty] | 0.05 | 0.047966 | 0.048771 | 0.04829 | 0.047816 | 0.047581 | [5 empty] | 0.05 | 0.047979 | 0.048771 | 0.048298 | 0.047831 | 0.0476
[6 empty] | 0.06 | 0.057087 | 0.058235 | 0.057549 | 0.056874 | 0.05654 | [5 empty] | 0.06 | 0.057109 | 0.058235 | 0.057562 | 0.056899 | 0.056572
[6 empty] | 0.07 | 0.066056 | 0.067606 | 0.066679 | 0.06577 | 0.065321 | [5 empty] | 0.07 | 0.066091 | 0.067606 | 0.0667 | 0.06581 | 0.065371
[6 empty] | 0.08 | 0.074877 | 0.076884 | 0.075683 | 0.074507 | 0.073928 | [5 empty] | 0.08 | 0.074928 | 0.076884 | 0.075713 | 0.074566 | 0.074001
[6 empty] | 0.09 | 0.083552 | 0.086069 | 0.084561 | 0.083088 | 0.082365 | [5 empty] | 0.09 | 0.083622 | 0.086069 | 0.084604 | 0.083171 | 0.082467
[6 empty] | 0.1 | 0.092082 | 0.095163 | 0.093316 | 0.091517 | 0.090635 | [5 empty] | 0.1 | 0.092177 | 0.095163 | 0.093374 | 0.091628 | 0.090772
[6 empty] | 0.2 | 0.16998 | 0.18127 | 0.17444 | 0.16796 | 0.16484 | [5 empty] | 0.2 | 0.17063 | 0.18127 | 0.17485 | 0.16871 | 0.16575
[6 empty] | 0.4 | 0.29162 | 0.32968 | 0.30628 | 0.28514 | 0.27534 | [5 empty] | 0.4 | 0.29544 | 0.32968 | 0.30878 | 0.28948 | 0.2804
[6 empty] | 0.6 | 0.37866 | 0.45119 | 0.40592 | 0.36689 | 0.3494 | [5 empty] | 0.6 | 0.38831 | 0.45119 | 0.4125 | 0.37766 | 0.3616
[6 empty] | 0.8 | 0.44095 | 0.55067 | 0.48123 | 0.42393 | 0.39905 | [5 empty] | 0.8 | 0.45831 | 0.55067 | 0.49349 | 0.44297 | 0.42007
[6 empty] | 1 | 0.48553 | 0.63212 | 0.53815 | 0.46372 | 0.43233 | [5 empty] | 1 | 0.51156 | 0.63212 | 0.55715 | 0.49187 | 0.46267
[6 empty] | 1.5 | 0.54911 | 0.77687 | 0.62682 | 0.51822 | 0.47511 | [5 empty] | 1.5 | 0.59678 | 0.77687 | 0.66413 | 0.56816 | 0.52639
[6 empty] | 2 | 0.57665 | 0.86466 | 0.67085 | 0.54038 | 0.49084 | [5 empty] | 2 | 0.64181 | 0.86466 | 0.72471 | 0.607 | 0.55681
[6 empty] | 2.5 | 0.58858 | 0.91792 | 0.69272 | 0.54938 | 0.49663 | [5 empty] | 2.5 | 0.666 | 0.91792 | 0.75946 | 0.6271 | 0.57157
[6 empty] | 3 | 0.59375 | 0.95021 | 0.70357 | 0.55305 | 0.49876 | [5 empty] | 3 | 0.67909 | 0.95021 | 0.77953 | 0.6376 | 0.5788
[6 empty] | 3.5 | 0.59599 | 0.9698 | 0.70897 | 0.55454 | 0.49954 | [5 empty] | 3.5 | 0.68622 | 0.9698 | 0.79118 | 0.6431 | 0.58234
[6 empty] | 4 | 0.59696 | 0.98168 | 0.71164 | 0.55514 | 0.49983 | [5 empty] | 4 | 0.69011 | 0.98168 | 0.79795 | 0.646 | 0.58409
[6 empty] | 4.5 | 0.59738 | 0.98889 | 0.71297 | 0.55539 | 0.49994 | [5 empty] | 4.5 | 0.69224 | 0.98889 | 0.8019 | 0.64752 | 0.58495
[6 empty] | 5 | 0.59756 | 0.99326 | 0.71363 | 0.55549 | 0.49998 | [5 empty] | 5 | 0.6934 | 0.99326 | 0.8042 | 0.64832 | 0.58537
[6 empty] | 5.5 | 0.59764 | 0.99591 | 0.71396 | 0.55553 | 0.49999 | [5 empty] | 5.5 | 0.69404 | 0.99591 | 0.80554 | 0.64875 | 0.58558
[6 empty] | 6 | 0.59768 | 0.99752 | 0.71413 | 0.55554 | 0.5 | [5 empty] | 6 | 0.69439 | 0.99752 | 0.80632 | 0.64897 | 0.58569
[5 empty] | 2 | Double Pipe - Counter Flow | [6 empty] | Solution |  |  | 4 | 2 Shell, 4,8 Tube Passes | [5 empty] | Solution
[27 empty] | 1.2054 | 1 | 1.077 | 1.2806 | 1.4142
[7 empty] | 0.67308 | 0 | 0.4 | 0.8 | 1 |  | NTU | 2.381 |  |  |  | 0.67308 | 0 | 0.4 | 0.8 | 1 | NTU | 2.381 |  |  | 0.67308 | 0 | 0.4 | 0.8 | 1
[6 empty] | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05 |  | Epsilon | 0.78276 |  |  | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.991e-05 | Epsilon | 0.74633 |  | 5e-05 | 4.9998e-05 | 4.9999e-05 | 4.9998e-05 | 4.9998e-05 | 4.9998e-05
[6 empty] | 0.01 | 0.009917 | 0.0099502 | 0.0099305 | 0.0099108 | 0.009901 | [5 empty] | 0.01 | 0.009917 | 0.0099502 | 0.0099304 | 0.0099108 | 0.009901 |  |  |  | 0.005 | 0.0049792 | 0.0049875 | 0.0049825 | 0.0049776 | 0.0049751
[6 empty] | 0.02 | 0.019671 | 0.019801 | 0.019724 | 0.019646 | 0.019608 | [5 empty] | 0.02 | 0.019671 | 0.019801 | 0.019724 | 0.019646 | 0.019607 |  |  |  | 0.01 | 0.0099169 | 0.0099502 | 0.0099304 | 0.0099107 | 0.0099008
[6 empty] | 0.03 | 0.029265 | 0.029554 | 0.029382 | 0.029211 | 0.029126 | [5 empty] | 0.03 | 0.029265 | 0.029554 | 0.029382 | 0.02921 | 0.029125 |  |  |  | 0.015 | 0.014814 | 0.014888 | 0.014844 | 0.0148 | 0.014778
[6 empty] | 0.04 | 0.038704 | 0.039211 | 0.038909 | 0.03861 | 0.038462 | [5 empty] | 0.04 | 0.038703 | 0.039211 | 0.038908 | 0.038608 | 0.038459 |  |  |  | 0.02 | 0.01967 | 0.019801 | 0.019723 | 0.019645 | 0.019607
[6 empty] | 0.05 | 0.047992 | 0.048771 | 0.048306 | 0.047847 | 0.047619 | [5 empty] | 0.05 | 0.047988 | 0.048771 | 0.048304 | 0.047843 | 0.047614 |  |  |  | 0.025 | 0.024486 | 0.02469 | 0.024569 | 0.024448 | 0.024388
[6 empty] | 0.06 | 0.057131 | 0.058235 | 0.057576 | 0.056925 | 0.056604 | [5 empty] | 0.06 | 0.057125 | 0.058235 | 0.057572 | 0.056919 | 0.056596 |  |  |  | 0.03 | 0.029262 | 0.029554 | 0.02938 | 0.029208 | 0.029122 | NTU
[6 empty] | 0.07 | 0.066125 | 0.067606 | 0.066721 | 0.06585 | 0.065421 | [5 empty] | 0.07 | 0.066116 | 0.067606 | 0.066716 | 0.06584 | 0.065408 |  |  |  | 0.035 | 0.033999 | 0.034395 | 0.034159 | 0.033926 | 0.03381 | Epsilon
[6 empty] | 0.08 | 0.074978 | 0.076884 | 0.075744 | 0.074625 | 0.074074 | [5 empty] | 0.08 | 0.074965 | 0.076884 | 0.075736 | 0.074611 | 0.074056 |  |  |  | 0.04 | 0.038698 | 0.039211 | 0.038905 | 0.038602 | 0.038452
[6 empty] | 0.09 | 0.083693 | 0.086069 | 0.084647 | 0.083254 | 0.082569 | [5 empty] | 0.09 | 0.083675 | 0.086069 | 0.084636 | 0.083233 | 0.082543 |  |  |  | 0.045 | 0.043357 | 0.044003 | 0.043618 | 0.043237 | 0.043048
[6 empty] | 0.1 | 0.092273 | 0.095163 | 0.093432 | 0.09174 | 0.090909 | [5 empty] | 0.1 | 0.092249 | 0.095163 | 0.093417 | 0.091712 | 0.090875 |  |  |  | 0.05 | 0.047979 | 0.048771 | 0.048298 | 0.047831 | 0.0476
[6 empty] | 0.2 | 0.17128 | 0.18127 | 0.17525 | 0.16947 | 0.16667 | [5 empty] | 0.2 | 0.17112 | 0.18127 | 0.17515 | 0.16928 | 0.16644 |  |  |  | 0.1 | 0.092177 | 0.095163 | 0.093374 | 0.091628 | 0.090772
[6 empty] | 0.4 | 0.29939 | 0.32968 | 0.31133 | 0.294 | 0.28571 | [5 empty] | 0.4 | 0.29839 | 0.32968 | 0.31069 | 0.29286 | 0.28436 |  |  |  | 0.2 | 0.17063 | 0.18127 | 0.17485 | 0.16871 | 0.16575
[6 empty] | 0.6 | 0.39864 | 0.45119 | 0.41935 | 0.38931 | 0.375 | [5 empty] | 0.6 | 0.39599 | 0.45119 | 0.41762 | 0.38631 | 0.37153 |  |  |  | 0.3 | 0.23775 | 0.25918 | 0.24617 | 0.23396 | 0.22814
[6 empty] | 0.8 | 0.47763 | 0.55067 | 0.50661 | 0.46454 | 0.44444 | [5 empty] | 0.8 | 0.47261 | 0.55067 | 0.50327 | 0.45889 | 0.43799 |  |  |  | 0.4 | 0.29544 | 0.32968 | 0.30878 | 0.28948 | 0.2804
[6 empty] | 1 | 0.54188 | 0.63212 | 0.57809 | 0.52539 | 0.5 | [5 empty] | 1 | 0.53387 | 0.63212 | 0.57273 | 0.51643 | 0.48988 |  |  |  | 0.5 | 0.34522 | 0.39347 | 0.36389 | 0.33694 | 0.3244
[6 empty] | 1.5 | 0.65941 | 0.77687 | 0.70868 | 0.63627 | 0.6 | [5 empty] | 1.5 | 0.6421 | 0.77687 | 0.69708 | 0.61704 | 0.5787 |  |  |  | 0.75 | 0.44258 | 0.52763 | 0.47505 | 0.4284 | 0.40716 |  | 1.1905
[6 empty] | 2 | 0.73843 | 0.86466 | 0.79453 | 0.71091 | 0.66667 | [5 empty] | 2 | 0.71042 | 0.86466 | 0.77608 | 0.67983 | 0.63264 |  |  |  | 1 | 0.51156 | 0.63212 | 0.55715 | 0.49187 | 0.46267 |  | 0.55067
[6 empty] | 2.5 | 0.79456 | 0.91792 | 0.853 | 0.76435 | 0.71429 | [5 empty] | 2.5 | 0.7555 | 0.91792 | 0.82801 | 0.72089 | 0.66706 |  |  |  | 1.25 | 0.56102 | 0.7135 | 0.6183 | 0.53649 | 0.50044
[6 empty] | 3 | 0.836 | 0.95021 | 0.8938 | 0.80433 | 0.75 | [5 empty] | 3 | 0.78615 | 0.95021 | 0.86303 | 0.74859 | 0.68972 |  |  |  | 1.5 | 0.59678 | 0.77687 | 0.66413 | 0.56816 | 0.52639
[6 empty] | 3.5 | 0.86748 | 0.9698 | 0.92274 | 0.83522 | 0.77778 | [5 empty] | 3.5 | 0.80745 | 0.9698 | 0.88715 | 0.76766 | 0.70495 |  |  |  | 1.75 | 0.6228 | 0.82623 | 0.69864 | 0.59077 | 0.54434
[6 empty] | 4 | 0.89191 | 0.98168 | 0.94352 | 0.8597 | 0.8 | [5 empty] | 4 | 0.82248 | 0.98168 | 0.90406 | 0.78099 | 0.71532 |  |  |  | 2 | 0.64181 | 0.86466 | 0.72471 | 0.607 | 0.55681
[6 empty] | 4.5 | 0.91119 | 0.98889 | 0.95856 | 0.87949 | 0.81818 | [5 empty] | 4.5 | 0.83322 | 0.98889 | 0.9161 | 0.79041 | 0.72245 |  |  |  | 2.25 | 0.65575 | 0.8946 | 0.74446 | 0.61867 | 0.5655
[6 empty] | 5 | 0.92661 | 0.99326 | 0.96952 | 0.89574 | 0.83333 | [5 empty] | 5 | 0.84096 | 0.99326 | 0.92479 | 0.79712 | 0.72739 |  |  |  | 2.5 | 0.666 | 0.91792 | 0.75946 | 0.6271 | 0.57157
[6 empty] | 5.5 | 0.93906 | 0.99591 | 0.97754 | 0.90926 | 0.84615 | [5 empty] | 5.5 | 0.84657 | 0.99591 | 0.93112 | 0.80192 | 0.73082 |  |  |  | 2.75 | 0.67354 | 0.93607 | 0.77085 | 0.63319 | 0.57582
[6 empty] | 6 | 0.94921 | 0.99752 | 0.98342 | 0.92064 | 0.85714 | [5 empty] | 6 | 0.85067 | 0.99752 | 0.93578 | 0.80536 | 0.73321 |  |  |  | 3 | 0.67909 | 0.95021 | 0.77953 | 0.6376 | 0.5788
[5 empty] | 5 | Cross Flow - Both Pass Unmixed | [6 empty] | Solution |  |  | 6 | Cross Flow - Lower Capacity Fluid Mixed | [5 empty] | Solution |  | 7 | Cross Flow - Higher Capacity Fluid Mixed
[7 empty] | 0.67308 | 0 | 0.4 | 0.8 | 1 |  | NTU | 2.381 |  |  |  | 0.67308 | 0 | 0.4 | 0.8 | 1 | NTU | 2.381 |  |  | 0.67308 | 0 | 0.4 | 0.8 | 1
[6 empty] | 0.0001 | 9.9969e-05 | 9.9995e-05 | 9.998e-05 | 9.9965e-05 | 9.9957e-05 |  | Epsilon | 0.7328 |  |  | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05 | Epsilon | 0.69472 |  | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05
[6 empty] | 0.01 | 0.009859 | 0.0099502 | 0.0098958 | 0.0098419 | 0.0098151 | [5 empty] | 0.01 | 0.0099169 | 0.0099502 | 0.0099304 | 0.0099107 | 0.0099008 |  |  |  | 0.01 | 0.0099169 | 0.0099502 | 0.0099304 | 0.0099107 | 0.0099008
[6 empty] | 0.02 | 0.019493 | 0.019801 | 0.019617 | 0.019435 | 0.019345 | [5 empty] | 0.02 | 0.01967 | 0.019801 | 0.019723 | 0.019645 | 0.019607 |  |  |  | 0.02 | 0.01967 | 0.019801 | 0.019723 | 0.019645 | 0.019607
[6 empty] | 0.03 | 0.028928 | 0.029554 | 0.02918 | 0.028811 | 0.02863 | [5 empty] | 0.03 | 0.029262 | 0.029554 | 0.02938 | 0.029208 | 0.029122 |  |  |  | 0.03 | 0.029262 | 0.029554 | 0.02938 | 0.029208 | 0.029122
[6 empty] | 0.04 | 0.038179 | 0.039211 | 0.038593 | 0.037988 | 0.03769 | [5 empty] | 0.04 | 0.038698 | 0.039211 | 0.038905 | 0.038602 | 0.038452 |  |  |  | 0.04 | 0.038698 | 0.039211 | 0.038905 | 0.038602 | 0.038452 | Solution
[6 empty] | 0.05 | 0.047255 | 0.048771 | 0.047863 | 0.046977 | 0.046542 | [5 empty] | 0.05 | 0.047979 | 0.048771 | 0.048298 | 0.047831 | 0.0476 |  |  |  | 0.05 | 0.047979 | 0.048771 | 0.048298 | 0.047831 | 0.0476
[6 empty] | 0.06 | 0.056166 | 0.058235 | 0.056994 | 0.055787 | 0.055196 | [5 empty] | 0.06 | 0.057109 | 0.058235 | 0.057563 | 0.0569 | 0.056572 |  |  |  | 0.06 | 0.057109 | 0.058235 | 0.057562 | 0.0569 | 0.056572 | NTU
[6 empty] | 0.07 | 0.064919 | 0.067606 | 0.065992 | 0.064428 | 0.063664 | [5 empty] | 0.07 | 0.066091 | 0.067606 | 0.0667 | 0.065811 | 0.065372 |  |  |  | 0.07 | 0.066091 | 0.067606 | 0.0667 | 0.06581 | 0.065372 | Epsilon
[6 empty] | 0.08 | 0.073518 | 0.076884 | 0.07486 | 0.072905 | 0.071953 | [5 empty] | 0.08 | 0.074929 | 0.076884 | 0.075714 | 0.074567 | 0.074002 |  |  |  | 0.08 | 0.074928 | 0.076884 | 0.075713 | 0.074567 | 0.074002
[6 empty] | 0.09 | 0.08197 | 0.086069 | 0.083601 | 0.081225 | 0.080071 | [5 empty] | 0.09 | 0.083624 | 0.086069 | 0.084605 | 0.083173 | 0.082469 |  |  |  | 0.09 | 0.083623 | 0.086069 | 0.084604 | 0.083173 | 0.082469
[6 empty] | 0.1 | 0.090279 | 0.095163 | 0.09222 | 0.089395 | 0.088025 | [5 empty] | 0.1 | 0.09218 | 0.095163 | 0.093375 | 0.091631 | 0.090775 |  |  |  | 0.1 | 0.092179 | 0.095163 | 0.093374 | 0.09163 | 0.090775
[6 empty] | 0.2 | 0.16639 | 0.18127 | 0.17223 | 0.16376 | 0.15973 | [5 empty] | 0.2 | 0.17066 | 0.18127 | 0.17487 | 0.16875 | 0.16579 |  |  |  | 0.2 | 0.17065 | 0.18127 | 0.17485 | 0.16874 | 0.16579
[6 empty] | 0.4 | 0.2888 | 0.32968 | 0.30461 | 0.28179 | 0.27117 | [5 empty] | 0.4 | 0.29579 | 0.32968 | 0.30902 | 0.28987 | 0.28085 |  |  |  | 0.4 | 0.29566 | 0.32968 | 0.30887 | 0.28979 | 0.28085
[6 empty] | 0.6 | 0.38291 | 0.45119 | 0.40915 | 0.37138 | 0.35404 | [5 empty] | 0.6 | 0.3896 | 0.45119 | 0.41341 | 0.37906 | 0.36313 |  |  |  | 0.6 | 0.38912 | 0.45119 | 0.41282 | 0.37873 | 0.36313
[6 empty] | 0.8 | 0.4572 | 0.55067 | 0.4931 | 0.44148 | 0.41793 | [5 empty] | 0.8 | 0.46129 | 0.55067 | 0.49572 | 0.44616 | 0.42344 |  |  |  | 0.8 | 0.46014 | 0.55067 | 0.49424 | 0.44539 | 0.42344
[6 empty] | 1 | 0.51703 | 0.63212 | 0.56141 | 0.49759 | 0.46854 | [5 empty] | 1 | 0.51703 | 0.63212 | 0.56141 | 0.49759 | 0.46854 |  |  |  | 1 | 0.51485 | 0.63212 | 0.55854 | 0.49614 | 0.46854
[6 empty] | 1.5 | 0.6244 | 0.77687 | 0.68475 | 0.59773 | 0.55782 | [5 empty] | 1.5 | 0.61108 | 0.77687 | 0.67631 | 0.58252 | 0.54016 |  |  |  | 1.5 | 0.60498 | 0.77687 | 0.66775 | 0.57857 | 0.54016 |  | 2.381
[6 empty] | 2 | 0.69446 | 0.86466 | 0.76466 | 0.66288 | 0.61541 | [5 empty] | 2 | 0.66682 | 0.86466 | 0.74758 | 0.63125 | 0.57881 |  |  |  | 2 | 0.65552 | 0.86466 | 0.73098 | 0.62411 | 0.57881 |  | 0.67913
[6 empty] | 2.5 | 0.74288 | 0.91792 | 0.81875 | 0.70801 | 0.65522 | [5 empty] | 2.5 | 0.70167 | 0.91792 | 0.79409 | 0.66069 | 0.60065 |  |  |  | 2.5 | 0.68474 | 0.91792 | 0.76826 | 0.65022 | 0.60065
[6 empty] | 3 | 0.77786 | 0.95021 | 0.85671 | 0.74076 | 0.68421 | [5 empty] | 3 | 0.72431 | 0.95021 | 0.82571 | 0.67909 | 0.61334 |  |  |  | 3 | 0.70197 | 0.95021 | 0.79049 | 0.66552 | 0.61334
[6 empty] | 3.5 | 0.80404 | 0.9698 | 0.88415 | 0.76545 | 0.70621 | [5 empty] | 3.5 | 0.73942 | 0.9698 | 0.84794 | 0.69087 | 0.62084 |  |  |  | 3.5 | 0.71223 | 0.9698 | 0.80384 | 0.67461 | 0.62084
[6 empty] | 4 | 0.82422 | 0.98168 | 0.90451 | 0.78464 | 0.72349 | [5 empty] | 4 | 0.7497 | 0.98168 | 0.86402 | 0.69852 | 0.62532 |  |  |  | 4 | 0.7184 | 0.98168 | 0.81188 | 0.68005 | 0.62532
[6 empty] | 4.5 | 0.84016 | 0.98889 | 0.91996 | 0.79995 | 0.73744 | [5 empty] | 4.5 | 0.75679 | 0.98889 | 0.87591 | 0.70354 | 0.62801 |  |  |  | 4.5 | 0.72211 | 0.98889 | 0.81674 | 0.68332 | 0.62801
[6 empty] | 5 | 0.85302 | 0.99326 | 0.93191 | 0.81242 | 0.74898 | [5 empty] | 5 | 0.76174 | 0.99326 | 0.88487 | 0.70686 | 0.62963 |  |  |  | 5 | 0.72435 | 0.99326 | 0.81968 | 0.6853 | 0.62963
[6 empty] | 5.5 | 0.86358 | 0.99591 | 0.94132 | 0.82279 | 0.75873 | [5 empty] | 5.5 | 0.76521 | 0.99591 | 0.89172 | 0.70906 | 0.63061 |  |  |  | 5.5 | 0.72571 | 0.99591 | 0.82146 | 0.6865 | 0.63061
[6 empty] | 6 | 0.8724 | 0.99752 | 0.94884 | 0.83155 | 0.76712 | [5 empty] | 6 | 0.76765 | 0.99752 | 0.89702 | 0.71053 | 0.63121 |  |  |  | 6 | 0.72653 | 0.99752 | 0.82254 | 0.68722 | 0.63121
[5 empty] | 8 | Cross Flow - Both Pass Mixed | [6 empty] | Solution
[7 empty] | 0.67308 | 0 | 0.4 | 0.8 | 1 |  | NTU | 2.381
[6 empty] | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05 |  | Epsilon | 0.65587
[6 empty] | 0.01 | 0.0099169 | 0.0099502 | 0.0099304 | 0.0099107 | 0.0099008
[6 empty] | 0.02 | 0.01967 | 0.019801 | 0.019723 | 0.019645 | 0.019607
[6 empty] | 0.03 | 0.029262 | 0.029554 | 0.02938 | 0.029208 | 0.029122
[6 empty] | 0.04 | 0.038698 | 0.039211 | 0.038905 | 0.038602 | 0.038452
[6 empty] | 0.05 | 0.047979 | 0.048771 | 0.048298 | 0.047831 | 0.0476
[6 empty] | 0.06 | 0.057109 | 0.058235 | 0.057562 | 0.056899 | 0.056572
[6 empty] | 0.07 | 0.066091 | 0.067606 | 0.0667 | 0.06581 | 0.065371
[6 empty] | 0.08 | 0.074928 | 0.076884 | 0.075713 | 0.074566 | 0.074001
[6 empty] | 0.09 | 0.083622 | 0.086069 | 0.084604 | 0.083171 | 0.082467
[6 empty] | 0.1 | 0.092177 | 0.095163 | 0.093374 | 0.091628 | 0.090772
[6 empty] | 0.2 | 0.17063 | 0.18127 | 0.17485 | 0.16871 | 0.16575
[6 empty] | 0.4 | 0.29543 | 0.32968 | 0.30878 | 0.28947 | 0.28039
[6 empty] | 0.6 | 0.38827 | 0.45119 | 0.41248 | 0.37761 | 0.36152
[6 empty] | 0.8 | 0.45818 | 0.55067 | 0.49343 | 0.4428 | 0.41983
[6 empty] | 1 | 0.51125 | 0.63212 | 0.55702 | 0.49146 | 0.46212
[6 empty] | 1.5 | 0.59543 | 0.77687 | 0.66353 | 0.56646 | 0.52417
[6 empty] | 2 | 0.63842 | 0.86466 | 0.72312 | 0.60281 | 0.55156
[6 empty] | 2.5 | 0.65956 | 0.91792 | 0.75631 | 0.61933 | 0.56216
[6 empty] | 3 | 0.66882 | 0.95021 | 0.77431 | 0.62544 | 0.56451
[6 empty] | 3.5 | 0.67159 | 0.9698 | 0.78349 | 0.62609 | 0.56289
[6 empty] | 4 | 0.67086 | 0.98168 | 0.7875 | 0.62397 | 0.5595
[6 empty] | 4.5 | 0.66831 | 0.98889 | 0.7885 | 0.62055 | 0.55548
[6 empty] | 5 | 0.66492 | 0.99326 | 0.78778 | 0.61663 | 0.5514
[6 empty] | 5.5 | 0.6612 | 0.99591 | 0.78608 | 0.61266 | 0.54753
[6 empty] | 6 | 0.65747 | 0.99752 | 0.78387 | 0.60884 | 0.54398

## SI
Heat Exchanger Analysis (Effectiveness - NTU Method)
CheGuide.com |  |  | Tag No. | E-102 |  |  | 1 | Double Pipe - Parallel Flow |  |  |  | 5
Chemical Engineer's Guide |  |  | Description | Product Cooler |  |  | 2 | Double Pipe - Counter Flow
|  |  | Date | 27-Dec-15 |  |  | 3 | Shell & Tube - 1 Shell - 2,4, .. Tube Passes
User Input |  |  | By | CheGuide |  |  | 4 | Shell & Tube - 2 Shell - 4,8,.. Tube Passes
[7 empty] | 5 | Cross Flow - Both Fluid Unmixed
Fluid Data |  | Hot | Cold |  |  |  | 6 | Cross Flow - Lower Capacity Fluid Mixed
Flowrate | kg/s | 0.62999 | 0.75599 |  |  |  | 7 | Cross Flow - Higher Capacity Fluid Mixed
Inlet Temperature | °C | 65.5556 | 15.5556 |  |  |  | 8 | Cross Flow - Both Fluid Mixed
Specific Heat | kJ/kg.°K | 1.7585 | 2.1771
[9 empty] | Hot | Cold
Exchanger Data | [5 empty] | Flowrate |  |  | 0.62999 | 0.75599 |  | Heat Rate | 40.5902 | BTU/h
Heat Exchanger Type |  | Cross Flow - Both Fluid Unmixed |  |  |  | Inlet Temperature |  |  | 65.5556 | 15.5556 |  | MTD | 15.3888 | oF
Heat Transfer Coefficient | kW/m².°K | 0.28391 |  |  |  | Outlet Temperature |  |  | 28.9155 | 40.2171 |  | DT1 | 25.3384
Area | m² | 9.2903 |  |  |  | Specific Heat |  |  | 1.7585 | 2.1771 |  | DT2 | 13.3599
[6 empty] | Heat Transfer Coefficient |  |  | 0.28391 |  |  | LMTD | 18.7146 | oF
Calculations | [5 empty] | Area |  |  | 9.2903 |  |  | F | 0.82229
Heat Transfer Conductance | kW/°K | 2.6376 |  |  |  | Conductance |  |  | 2.6376
Heat Transfer Rate | kW | 40.5902 |  |  |  | NTU |  |  | 2.381
Number of Transfer Units |  | 2.381 |  |  |  | Qmax |  |  | 55.3904 | BTU/h
Heat Capacity Ratio |  | 0.67308 |  |  |  | C_Hot | 1.1078 |  | C_Min | 1.1078 |  | Cr | 0.67308
Heat Exchanger Effectiveness |  | 0.7328 |  |  |  | C_Cold | 1.6459 |  | C_Max | 1.6459 |  | Epsilon | 0.7328
|  | Hot | Cold
Outlet Temperature | °C | 28.9155 | 40.2171
Flowrate * Specific Heat | kW/°K | 1.1078 | 1.6459 |  |  | Drawing Case | [6 empty] | Line 1 | Xaxis | Yaxis
Mean temperature Difference | °C | 15.3888 | [11 empty] | 2.381 | 0
LMTD | °C | 18.7146 |  |  |  | NTU | 0.67308 | 0 | 0.4 | 0.8 | 1 |  |  | 2.381 | 1
[6 empty] | 0.0001 | 9.9969e-05 | 9.9995e-05 | 9.998e-05 | 9.9965e-05 | 9.9957e-05
[6 empty] | 0.01 | 0.009859 | 0.0099502 | 0.0098958 | 0.0098419 | 0.0098151 |  | Line 2 | Xaxis | Yaxis
[6 empty] | 0.02 | 0.019493 | 0.019801 | 0.019617 | 0.019435 | 0.019345 |  |  | 0 | 0.7328
[6 empty] | 0.03 | 0.028928 | 0.029554 | 0.02918 | 0.028811 | 0.02863 |  |  | 6 | 0.7328
[6 empty] | 0.04 | 0.038179 | 0.039211 | 0.038593 | 0.037988 | 0.03769
[6 empty] | 0.05 | 0.047255 | 0.048771 | 0.047863 | 0.046977 | 0.046542
[6 empty] | 0.06 | 0.056166 | 0.058235 | 0.056994 | 0.055787 | 0.055196
[6 empty] | 0.07 | 0.064919 | 0.067606 | 0.065992 | 0.064428 | 0.063664
[6 empty] | 0.08 | 0.073518 | 0.076884 | 0.07486 | 0.072905 | 0.071953
[6 empty] | 0.09 | 0.08197 | 0.086069 | 0.083601 | 0.081225 | 0.080071
[6 empty] | 0.1 | 0.090279 | 0.095163 | 0.09222 | 0.089395 | 0.088025
[6 empty] | 0.2 | 0.16639 | 0.18127 | 0.17223 | 0.16376 | 0.15973
[6 empty] | 0.4 | 0.2888 | 0.32968 | 0.30461 | 0.28179 | 0.27117
[6 empty] | 0.6 | 0.38291 | 0.45119 | 0.40915 | 0.37138 | 0.35404
[6 empty] | 0.8 | 0.4572 | 0.55067 | 0.4931 | 0.44148 | 0.41793
[6 empty] | 1 | 0.51703 | 0.63212 | 0.56141 | 0.49759 | 0.46854
[6 empty] | 1.5 | 0.6244 | 0.77687 | 0.68475 | 0.59773 | 0.55782
[6 empty] | 2 | 0.69446 | 0.86466 | 0.76466 | 0.66288 | 0.61541
[6 empty] | 2.5 | 0.74288 | 0.91792 | 0.81875 | 0.70801 | 0.65522
[6 empty] | 3 | 0.77786 | 0.95021 | 0.85671 | 0.74076 | 0.68421
[6 empty] | 3.5 | 0.80404 | 0.9698 | 0.88415 | 0.76545 | 0.70621
[6 empty] | 4 | 0.82422 | 0.98168 | 0.90451 | 0.78464 | 0.72349
[6 empty] | 4.5 | 0.84016 | 0.98889 | 0.91996 | 0.79995 | 0.73744
[6 empty] | 5 | 0.85302 | 0.99326 | 0.93191 | 0.81242 | 0.74898
[6 empty] | 5.5 | 0.86358 | 0.99591 | 0.94132 | 0.82279 | 0.75873
[6 empty] | 6 | 0.8724 | 0.99752 | 0.94884 | 0.83155 | 0.76712
Calculation Phase
[5 empty] | 1 | Double Pipe - Parallel Flow | [6 empty] | Solution |  |  | 3 | 1 Shell, 2,4 Tube Passes | [5 empty] | Solution
[18 empty] | 1.2054 | 1 | 1.077 | 1.2806 | 1.4142
[7 empty] | 0.67308 | 0 | 0.4 | 0.8 | 1 |  | NTU | 2.381 |  |  |  | 0.67308 | 0 | 0.4 | 0.8 | 1 | NTU | 2.381
[6 empty] | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05 |  | Epsilon | 0.58657 |  |  | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05 | Epsilon | 0.66151
[6 empty] | 0.01 | 0.0099168 | 0.0099502 | 0.0099303 | 0.0099105 | 0.0099007 | [5 empty] | 0.01 | 0.0099169 | 0.0099502 | 0.0099304 | 0.0099107 | 0.0099008
[6 empty] | 0.02 | 0.019669 | 0.019801 | 0.019723 | 0.019644 | 0.019605 | [5 empty] | 0.02 | 0.01967 | 0.019801 | 0.019723 | 0.019645 | 0.019607
[6 empty] | 0.03 | 0.02926 | 0.029554 | 0.029379 | 0.029204 | 0.029118 | [5 empty] | 0.03 | 0.029262 | 0.029554 | 0.02938 | 0.029208 | 0.029122
[6 empty] | 0.04 | 0.038691 | 0.039211 | 0.038901 | 0.038594 | 0.038442 | [5 empty] | 0.04 | 0.038698 | 0.039211 | 0.038905 | 0.038602 | 0.038452
[6 empty] | 0.05 | 0.047966 | 0.048771 | 0.04829 | 0.047816 | 0.047581 | [5 empty] | 0.05 | 0.047979 | 0.048771 | 0.048298 | 0.047831 | 0.0476
[6 empty] | 0.06 | 0.057087 | 0.058235 | 0.057549 | 0.056874 | 0.05654 | [5 empty] | 0.06 | 0.057109 | 0.058235 | 0.057562 | 0.056899 | 0.056572
[6 empty] | 0.07 | 0.066056 | 0.067606 | 0.066679 | 0.06577 | 0.065321 | [5 empty] | 0.07 | 0.066091 | 0.067606 | 0.0667 | 0.06581 | 0.065371
[6 empty] | 0.08 | 0.074877 | 0.076884 | 0.075683 | 0.074507 | 0.073928 | [5 empty] | 0.08 | 0.074928 | 0.076884 | 0.075713 | 0.074566 | 0.074001
[6 empty] | 0.09 | 0.083552 | 0.086069 | 0.084561 | 0.083088 | 0.082365 | [5 empty] | 0.09 | 0.083622 | 0.086069 | 0.084604 | 0.083171 | 0.082467
[6 empty] | 0.1 | 0.092082 | 0.095163 | 0.093316 | 0.091517 | 0.090635 | [5 empty] | 0.1 | 0.092177 | 0.095163 | 0.093374 | 0.091628 | 0.090772
[6 empty] | 0.2 | 0.16998 | 0.18127 | 0.17444 | 0.16796 | 0.16484 | [5 empty] | 0.2 | 0.17063 | 0.18127 | 0.17485 | 0.16871 | 0.16575
[6 empty] | 0.4 | 0.29162 | 0.32968 | 0.30628 | 0.28514 | 0.27534 | [5 empty] | 0.4 | 0.29544 | 0.32968 | 0.30878 | 0.28948 | 0.2804
[6 empty] | 0.6 | 0.37866 | 0.45119 | 0.40592 | 0.36689 | 0.3494 | [5 empty] | 0.6 | 0.38831 | 0.45119 | 0.4125 | 0.37766 | 0.3616
[6 empty] | 0.8 | 0.44095 | 0.55067 | 0.48123 | 0.42393 | 0.39905 | [5 empty] | 0.8 | 0.45831 | 0.55067 | 0.49349 | 0.44297 | 0.42007
[6 empty] | 1 | 0.48553 | 0.63212 | 0.53815 | 0.46372 | 0.43233 | [5 empty] | 1 | 0.51156 | 0.63212 | 0.55715 | 0.49187 | 0.46267
[6 empty] | 1.5 | 0.54911 | 0.77687 | 0.62682 | 0.51822 | 0.47511 | [5 empty] | 1.5 | 0.59678 | 0.77687 | 0.66413 | 0.56816 | 0.52639
[6 empty] | 2 | 0.57665 | 0.86466 | 0.67085 | 0.54038 | 0.49084 | [5 empty] | 2 | 0.64181 | 0.86466 | 0.72471 | 0.607 | 0.55681
[6 empty] | 2.5 | 0.58858 | 0.91792 | 0.69272 | 0.54938 | 0.49663 | [5 empty] | 2.5 | 0.666 | 0.91792 | 0.75946 | 0.6271 | 0.57157
[6 empty] | 3 | 0.59375 | 0.95021 | 0.70357 | 0.55305 | 0.49876 | [5 empty] | 3 | 0.67909 | 0.95021 | 0.77953 | 0.6376 | 0.5788
[6 empty] | 3.5 | 0.59599 | 0.9698 | 0.70897 | 0.55454 | 0.49954 | [5 empty] | 3.5 | 0.68622 | 0.9698 | 0.79118 | 0.6431 | 0.58234
[6 empty] | 4 | 0.59696 | 0.98168 | 0.71164 | 0.55514 | 0.49983 | [5 empty] | 4 | 0.69011 | 0.98168 | 0.79795 | 0.646 | 0.58409
[6 empty] | 4.5 | 0.59738 | 0.98889 | 0.71297 | 0.55539 | 0.49994 | [5 empty] | 4.5 | 0.69224 | 0.98889 | 0.8019 | 0.64752 | 0.58495
[6 empty] | 5 | 0.59756 | 0.99326 | 0.71363 | 0.55549 | 0.49998 | [5 empty] | 5 | 0.6934 | 0.99326 | 0.8042 | 0.64832 | 0.58537
[6 empty] | 5.5 | 0.59764 | 0.99591 | 0.71396 | 0.55553 | 0.49999 | [5 empty] | 5.5 | 0.69404 | 0.99591 | 0.80554 | 0.64875 | 0.58558
[6 empty] | 6 | 0.59768 | 0.99752 | 0.71413 | 0.55554 | 0.5 | [5 empty] | 6 | 0.69439 | 0.99752 | 0.80632 | 0.64897 | 0.58569
[5 empty] | 2 | Double Pipe - Counter Flow | [6 empty] | Solution |  |  | 4 | 2 Shell, 4,8 Tube Passes | [5 empty] | Solution
[27 empty] | 1.2054 | 1 | 1.077 | 1.2806 | 1.4142
[7 empty] | 0.67308 | 0 | 0.4 | 0.8 | 1 |  | NTU | 2.381 |  |  |  | 0.67308 | 0 | 0.4 | 0.8 | 1 | NTU | 2.381 |  |  | 0.67308 | 0 | 0.4 | 0.8 | 1
[6 empty] | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05 |  | Epsilon | 0.78276 |  |  | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.991e-05 | Epsilon | 0.74633 |  | 5e-05 | 4.9998e-05 | 4.9999e-05 | 4.9998e-05 | 4.9998e-05 | 4.9998e-05
[6 empty] | 0.01 | 0.009917 | 0.0099502 | 0.0099305 | 0.0099108 | 0.009901 | [5 empty] | 0.01 | 0.009917 | 0.0099502 | 0.0099304 | 0.0099108 | 0.009901 |  |  |  | 0.005 | 0.0049792 | 0.0049875 | 0.0049825 | 0.0049776 | 0.0049751
[6 empty] | 0.02 | 0.019671 | 0.019801 | 0.019724 | 0.019646 | 0.019608 | [5 empty] | 0.02 | 0.019671 | 0.019801 | 0.019724 | 0.019646 | 0.019607 |  |  |  | 0.01 | 0.0099169 | 0.0099502 | 0.0099304 | 0.0099107 | 0.0099008
[6 empty] | 0.03 | 0.029265 | 0.029554 | 0.029382 | 0.029211 | 0.029126 | [5 empty] | 0.03 | 0.029265 | 0.029554 | 0.029382 | 0.02921 | 0.029125 |  |  |  | 0.015 | 0.014814 | 0.014888 | 0.014844 | 0.0148 | 0.014778
[6 empty] | 0.04 | 0.038704 | 0.039211 | 0.038909 | 0.03861 | 0.038462 | [5 empty] | 0.04 | 0.038703 | 0.039211 | 0.038908 | 0.038608 | 0.038459 |  |  |  | 0.02 | 0.01967 | 0.019801 | 0.019723 | 0.019645 | 0.019607
[6 empty] | 0.05 | 0.047992 | 0.048771 | 0.048306 | 0.047847 | 0.047619 | [5 empty] | 0.05 | 0.047988 | 0.048771 | 0.048304 | 0.047843 | 0.047614 |  |  |  | 0.025 | 0.024486 | 0.02469 | 0.024569 | 0.024448 | 0.024388
[6 empty] | 0.06 | 0.057131 | 0.058235 | 0.057576 | 0.056925 | 0.056604 | [5 empty] | 0.06 | 0.057125 | 0.058235 | 0.057572 | 0.056919 | 0.056596 |  |  |  | 0.03 | 0.029262 | 0.029554 | 0.02938 | 0.029208 | 0.029122 | NTU
[6 empty] | 0.07 | 0.066125 | 0.067606 | 0.066721 | 0.06585 | 0.065421 | [5 empty] | 0.07 | 0.066116 | 0.067606 | 0.066716 | 0.06584 | 0.065408 |  |  |  | 0.035 | 0.033999 | 0.034395 | 0.034159 | 0.033926 | 0.03381 | Epsilon
[6 empty] | 0.08 | 0.074978 | 0.076884 | 0.075744 | 0.074625 | 0.074074 | [5 empty] | 0.08 | 0.074965 | 0.076884 | 0.075736 | 0.074611 | 0.074056 |  |  |  | 0.04 | 0.038698 | 0.039211 | 0.038905 | 0.038602 | 0.038452
[6 empty] | 0.09 | 0.083693 | 0.086069 | 0.084647 | 0.083254 | 0.082569 | [5 empty] | 0.09 | 0.083675 | 0.086069 | 0.084636 | 0.083233 | 0.082543 |  |  |  | 0.045 | 0.043357 | 0.044003 | 0.043618 | 0.043237 | 0.043048
[6 empty] | 0.1 | 0.092273 | 0.095163 | 0.093432 | 0.09174 | 0.090909 | [5 empty] | 0.1 | 0.092249 | 0.095163 | 0.093417 | 0.091712 | 0.090875 |  |  |  | 0.05 | 0.047979 | 0.048771 | 0.048298 | 0.047831 | 0.0476
[6 empty] | 0.2 | 0.17128 | 0.18127 | 0.17525 | 0.16947 | 0.16667 | [5 empty] | 0.2 | 0.17112 | 0.18127 | 0.17515 | 0.16928 | 0.16644 |  |  |  | 0.1 | 0.092177 | 0.095163 | 0.093374 | 0.091628 | 0.090772
[6 empty] | 0.4 | 0.29939 | 0.32968 | 0.31133 | 0.294 | 0.28571 | [5 empty] | 0.4 | 0.29839 | 0.32968 | 0.31069 | 0.29286 | 0.28436 |  |  |  | 0.2 | 0.17063 | 0.18127 | 0.17485 | 0.16871 | 0.16575
[6 empty] | 0.6 | 0.39864 | 0.45119 | 0.41935 | 0.38931 | 0.375 | [5 empty] | 0.6 | 0.39599 | 0.45119 | 0.41762 | 0.38631 | 0.37153 |  |  |  | 0.3 | 0.23775 | 0.25918 | 0.24617 | 0.23396 | 0.22814
[6 empty] | 0.8 | 0.47763 | 0.55067 | 0.50661 | 0.46454 | 0.44444 | [5 empty] | 0.8 | 0.47261 | 0.55067 | 0.50327 | 0.45889 | 0.43799 |  |  |  | 0.4 | 0.29544 | 0.32968 | 0.30878 | 0.28948 | 0.2804
[6 empty] | 1 | 0.54188 | 0.63212 | 0.57809 | 0.52539 | 0.5 | [5 empty] | 1 | 0.53387 | 0.63212 | 0.57273 | 0.51643 | 0.48988 |  |  |  | 0.5 | 0.34522 | 0.39347 | 0.36389 | 0.33694 | 0.3244
[6 empty] | 1.5 | 0.65941 | 0.77687 | 0.70868 | 0.63627 | 0.6 | [5 empty] | 1.5 | 0.6421 | 0.77687 | 0.69708 | 0.61704 | 0.5787 |  |  |  | 0.75 | 0.44258 | 0.52763 | 0.47505 | 0.4284 | 0.40716 |  | 1.1905
[6 empty] | 2 | 0.73843 | 0.86466 | 0.79453 | 0.71091 | 0.66667 | [5 empty] | 2 | 0.71042 | 0.86466 | 0.77608 | 0.67983 | 0.63264 |  |  |  | 1 | 0.51156 | 0.63212 | 0.55715 | 0.49187 | 0.46267 |  | 0.55067
[6 empty] | 2.5 | 0.79456 | 0.91792 | 0.853 | 0.76435 | 0.71429 | [5 empty] | 2.5 | 0.7555 | 0.91792 | 0.82801 | 0.72089 | 0.66706 |  |  |  | 1.25 | 0.56102 | 0.7135 | 0.6183 | 0.53649 | 0.50044
[6 empty] | 3 | 0.836 | 0.95021 | 0.8938 | 0.80433 | 0.75 | [5 empty] | 3 | 0.78615 | 0.95021 | 0.86303 | 0.74859 | 0.68972 |  |  |  | 1.5 | 0.59678 | 0.77687 | 0.66413 | 0.56816 | 0.52639
[6 empty] | 3.5 | 0.86748 | 0.9698 | 0.92274 | 0.83522 | 0.77778 | [5 empty] | 3.5 | 0.80745 | 0.9698 | 0.88715 | 0.76766 | 0.70495 |  |  |  | 1.75 | 0.6228 | 0.82623 | 0.69864 | 0.59077 | 0.54434
[6 empty] | 4 | 0.89191 | 0.98168 | 0.94352 | 0.8597 | 0.8 | [5 empty] | 4 | 0.82248 | 0.98168 | 0.90406 | 0.78099 | 0.71532 |  |  |  | 2 | 0.64181 | 0.86466 | 0.72471 | 0.607 | 0.55681
[6 empty] | 4.5 | 0.91119 | 0.98889 | 0.95856 | 0.87949 | 0.81818 | [5 empty] | 4.5 | 0.83322 | 0.98889 | 0.9161 | 0.79041 | 0.72245 |  |  |  | 2.25 | 0.65575 | 0.8946 | 0.74446 | 0.61867 | 0.5655
[6 empty] | 5 | 0.92661 | 0.99326 | 0.96952 | 0.89574 | 0.83333 | [5 empty] | 5 | 0.84096 | 0.99326 | 0.92479 | 0.79712 | 0.72739 |  |  |  | 2.5 | 0.666 | 0.91792 | 0.75946 | 0.6271 | 0.57157
[6 empty] | 5.5 | 0.93906 | 0.99591 | 0.97754 | 0.90926 | 0.84615 | [5 empty] | 5.5 | 0.84657 | 0.99591 | 0.93112 | 0.80192 | 0.73082 |  |  |  | 2.75 | 0.67354 | 0.93607 | 0.77085 | 0.63319 | 0.57582
[6 empty] | 6 | 0.94921 | 0.99752 | 0.98342 | 0.92064 | 0.85714 | [5 empty] | 6 | 0.85067 | 0.99752 | 0.93578 | 0.80536 | 0.73321 |  |  |  | 3 | 0.67909 | 0.95021 | 0.77953 | 0.6376 | 0.5788
[5 empty] | 5 | Cross Flow - Both Pass Unmixed | [6 empty] | Solution |  |  | 6 | Cross Flow - Lower Capacity Fluid Mixed | [5 empty] | Solution |  | 7 | Cross Flow - Higher Capacity Fluid Mixed
[7 empty] | 0.67308 | 0 | 0.4 | 0.8 | 1 |  | NTU | 2.381 |  |  |  | 0.67308 | 0 | 0.4 | 0.8 | 1 | NTU | 2.381 |  |  | 0.67308 | 0 | 0.4 | 0.8 | 1
[6 empty] | 0.0001 | 9.9969e-05 | 9.9995e-05 | 9.998e-05 | 9.9965e-05 | 9.9957e-05 |  | Epsilon | 0.7328 |  |  | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05 | Epsilon | 0.69472 |  | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05
[6 empty] | 0.01 | 0.009859 | 0.0099502 | 0.0098958 | 0.0098419 | 0.0098151 | [5 empty] | 0.01 | 0.0099169 | 0.0099502 | 0.0099304 | 0.0099107 | 0.0099008 |  |  |  | 0.01 | 0.0099169 | 0.0099502 | 0.0099304 | 0.0099107 | 0.0099008
[6 empty] | 0.02 | 0.019493 | 0.019801 | 0.019617 | 0.019435 | 0.019345 | [5 empty] | 0.02 | 0.01967 | 0.019801 | 0.019723 | 0.019645 | 0.019607 |  |  |  | 0.02 | 0.01967 | 0.019801 | 0.019723 | 0.019645 | 0.019607
[6 empty] | 0.03 | 0.028928 | 0.029554 | 0.02918 | 0.028811 | 0.02863 | [5 empty] | 0.03 | 0.029262 | 0.029554 | 0.02938 | 0.029208 | 0.029122 |  |  |  | 0.03 | 0.029262 | 0.029554 | 0.02938 | 0.029208 | 0.029122
[6 empty] | 0.04 | 0.038179 | 0.039211 | 0.038593 | 0.037988 | 0.03769 | [5 empty] | 0.04 | 0.038698 | 0.039211 | 0.038905 | 0.038602 | 0.038452 |  |  |  | 0.04 | 0.038698 | 0.039211 | 0.038905 | 0.038602 | 0.038452 | Solution
[6 empty] | 0.05 | 0.047255 | 0.048771 | 0.047863 | 0.046977 | 0.046542 | [5 empty] | 0.05 | 0.047979 | 0.048771 | 0.048298 | 0.047831 | 0.0476 |  |  |  | 0.05 | 0.047979 | 0.048771 | 0.048298 | 0.047831 | 0.0476
[6 empty] | 0.06 | 0.056166 | 0.058235 | 0.056994 | 0.055787 | 0.055196 | [5 empty] | 0.06 | 0.057109 | 0.058235 | 0.057563 | 0.0569 | 0.056572 |  |  |  | 0.06 | 0.057109 | 0.058235 | 0.057562 | 0.0569 | 0.056572 | NTU
[6 empty] | 0.07 | 0.064919 | 0.067606 | 0.065992 | 0.064428 | 0.063664 | [5 empty] | 0.07 | 0.066091 | 0.067606 | 0.0667 | 0.065811 | 0.065372 |  |  |  | 0.07 | 0.066091 | 0.067606 | 0.0667 | 0.06581 | 0.065372 | Epsilon
[6 empty] | 0.08 | 0.073518 | 0.076884 | 0.07486 | 0.072905 | 0.071953 | [5 empty] | 0.08 | 0.074929 | 0.076884 | 0.075714 | 0.074567 | 0.074002 |  |  |  | 0.08 | 0.074928 | 0.076884 | 0.075713 | 0.074567 | 0.074002
[6 empty] | 0.09 | 0.08197 | 0.086069 | 0.083601 | 0.081225 | 0.080071 | [5 empty] | 0.09 | 0.083624 | 0.086069 | 0.084605 | 0.083173 | 0.082469 |  |  |  | 0.09 | 0.083623 | 0.086069 | 0.084604 | 0.083173 | 0.082469
[6 empty] | 0.1 | 0.090279 | 0.095163 | 0.09222 | 0.089395 | 0.088025 | [5 empty] | 0.1 | 0.09218 | 0.095163 | 0.093375 | 0.091631 | 0.090775 |  |  |  | 0.1 | 0.092179 | 0.095163 | 0.093374 | 0.09163 | 0.090775
[6 empty] | 0.2 | 0.16639 | 0.18127 | 0.17223 | 0.16376 | 0.15973 | [5 empty] | 0.2 | 0.17066 | 0.18127 | 0.17487 | 0.16875 | 0.16579 |  |  |  | 0.2 | 0.17065 | 0.18127 | 0.17485 | 0.16874 | 0.16579
[6 empty] | 0.4 | 0.2888 | 0.32968 | 0.30461 | 0.28179 | 0.27117 | [5 empty] | 0.4 | 0.29579 | 0.32968 | 0.30902 | 0.28987 | 0.28085 |  |  |  | 0.4 | 0.29566 | 0.32968 | 0.30887 | 0.28979 | 0.28085
[6 empty] | 0.6 | 0.38291 | 0.45119 | 0.40915 | 0.37138 | 0.35404 | [5 empty] | 0.6 | 0.3896 | 0.45119 | 0.41341 | 0.37906 | 0.36313 |  |  |  | 0.6 | 0.38912 | 0.45119 | 0.41282 | 0.37873 | 0.36313
[6 empty] | 0.8 | 0.4572 | 0.55067 | 0.4931 | 0.44148 | 0.41793 | [5 empty] | 0.8 | 0.46129 | 0.55067 | 0.49572 | 0.44616 | 0.42344 |  |  |  | 0.8 | 0.46014 | 0.55067 | 0.49424 | 0.44539 | 0.42344
[6 empty] | 1 | 0.51703 | 0.63212 | 0.56141 | 0.49759 | 0.46854 | [5 empty] | 1 | 0.51703 | 0.63212 | 0.56141 | 0.49759 | 0.46854 |  |  |  | 1 | 0.51485 | 0.63212 | 0.55854 | 0.49614 | 0.46854
[6 empty] | 1.5 | 0.6244 | 0.77687 | 0.68475 | 0.59773 | 0.55782 | [5 empty] | 1.5 | 0.61108 | 0.77687 | 0.67631 | 0.58252 | 0.54016 |  |  |  | 1.5 | 0.60498 | 0.77687 | 0.66775 | 0.57857 | 0.54016 |  | 2.381
[6 empty] | 2 | 0.69446 | 0.86466 | 0.76466 | 0.66288 | 0.61541 | [5 empty] | 2 | 0.66682 | 0.86466 | 0.74758 | 0.63125 | 0.57881 |  |  |  | 2 | 0.65552 | 0.86466 | 0.73098 | 0.62411 | 0.57881 |  | 0.67913
[6 empty] | 2.5 | 0.74288 | 0.91792 | 0.81875 | 0.70801 | 0.65522 | [5 empty] | 2.5 | 0.70167 | 0.91792 | 0.79409 | 0.66069 | 0.60065 |  |  |  | 2.5 | 0.68474 | 0.91792 | 0.76826 | 0.65022 | 0.60065
[6 empty] | 3 | 0.77786 | 0.95021 | 0.85671 | 0.74076 | 0.68421 | [5 empty] | 3 | 0.72431 | 0.95021 | 0.82571 | 0.67909 | 0.61334 |  |  |  | 3 | 0.70197 | 0.95021 | 0.79049 | 0.66552 | 0.61334
[6 empty] | 3.5 | 0.80404 | 0.9698 | 0.88415 | 0.76545 | 0.70621 | [5 empty] | 3.5 | 0.73942 | 0.9698 | 0.84794 | 0.69087 | 0.62084 |  |  |  | 3.5 | 0.71223 | 0.9698 | 0.80384 | 0.67461 | 0.62084
[6 empty] | 4 | 0.82422 | 0.98168 | 0.90451 | 0.78464 | 0.72349 | [5 empty] | 4 | 0.7497 | 0.98168 | 0.86402 | 0.69852 | 0.62532 |  |  |  | 4 | 0.7184 | 0.98168 | 0.81188 | 0.68005 | 0.62532
[6 empty] | 4.5 | 0.84016 | 0.98889 | 0.91996 | 0.79995 | 0.73744 | [5 empty] | 4.5 | 0.75679 | 0.98889 | 0.87591 | 0.70354 | 0.62801 |  |  |  | 4.5 | 0.72211 | 0.98889 | 0.81674 | 0.68332 | 0.62801
[6 empty] | 5 | 0.85302 | 0.99326 | 0.93191 | 0.81242 | 0.74898 | [5 empty] | 5 | 0.76174 | 0.99326 | 0.88487 | 0.70686 | 0.62963 |  |  |  | 5 | 0.72435 | 0.99326 | 0.81968 | 0.6853 | 0.62963
[6 empty] | 5.5 | 0.86358 | 0.99591 | 0.94132 | 0.82279 | 0.75873 | [5 empty] | 5.5 | 0.76521 | 0.99591 | 0.89172 | 0.70906 | 0.63061 |  |  |  | 5.5 | 0.72571 | 0.99591 | 0.82146 | 0.6865 | 0.63061
[6 empty] | 6 | 0.8724 | 0.99752 | 0.94884 | 0.83155 | 0.76712 | [5 empty] | 6 | 0.76765 | 0.99752 | 0.89702 | 0.71053 | 0.63121 |  |  |  | 6 | 0.72653 | 0.99752 | 0.82254 | 0.68722 | 0.63121
[5 empty] | 8 | Cross Flow - Both Pass Mixed | [6 empty] | Solution
[7 empty] | 0.67308 | 0 | 0.4 | 0.8 | 1 |  | NTU | 2.381
[6 empty] | 0.0001 | 9.9992e-05 | 9.9995e-05 | 9.9993e-05 | 9.9991e-05 | 9.999e-05 |  | Epsilon | 0.65587
[6 empty] | 0.01 | 0.0099169 | 0.0099502 | 0.0099304 | 0.0099107 | 0.0099008
[6 empty] | 0.02 | 0.01967 | 0.019801 | 0.019723 | 0.019645 | 0.019607
[6 empty] | 0.03 | 0.029262 | 0.029554 | 0.02938 | 0.029208 | 0.029122
[6 empty] | 0.04 | 0.038698 | 0.039211 | 0.038905 | 0.038602 | 0.038452
[6 empty] | 0.05 | 0.047979 | 0.048771 | 0.048298 | 0.047831 | 0.0476
[6 empty] | 0.06 | 0.057109 | 0.058235 | 0.057562 | 0.056899 | 0.056572
[6 empty] | 0.07 | 0.066091 | 0.067606 | 0.0667 | 0.06581 | 0.065371
[6 empty] | 0.08 | 0.074928 | 0.076884 | 0.075713 | 0.074566 | 0.074001
[6 empty] | 0.09 | 0.083622 | 0.086069 | 0.084604 | 0.083171 | 0.082467
[6 empty] | 0.1 | 0.092177 | 0.095163 | 0.093374 | 0.091628 | 0.090772
[6 empty] | 0.2 | 0.17063 | 0.18127 | 0.17485 | 0.16871 | 0.16575
[6 empty] | 0.4 | 0.29543 | 0.32968 | 0.30878 | 0.28947 | 0.28039
[6 empty] | 0.6 | 0.38827 | 0.45119 | 0.41248 | 0.37761 | 0.36152
[6 empty] | 0.8 | 0.45818 | 0.55067 | 0.49343 | 0.4428 | 0.41983
[6 empty] | 1 | 0.51125 | 0.63212 | 0.55702 | 0.49146 | 0.46212
[6 empty] | 1.5 | 0.59543 | 0.77687 | 0.66353 | 0.56646 | 0.52417
[6 empty] | 2 | 0.63842 | 0.86466 | 0.72312 | 0.60281 | 0.55156
[6 empty] | 2.5 | 0.65956 | 0.91792 | 0.75631 | 0.61933 | 0.56216
[6 empty] | 3 | 0.66882 | 0.95021 | 0.77431 | 0.62544 | 0.56451
[6 empty] | 3.5 | 0.67159 | 0.9698 | 0.78349 | 0.62609 | 0.56289
[6 empty] | 4 | 0.67086 | 0.98168 | 0.7875 | 0.62397 | 0.5595
[6 empty] | 4.5 | 0.66831 | 0.98889 | 0.7885 | 0.62055 | 0.55548
[6 empty] | 5 | 0.66492 | 0.99326 | 0.78778 | 0.61663 | 0.5514
[6 empty] | 5.5 | 0.6612 | 0.99591 | 0.78608 | 0.61266 | 0.54753
[6 empty] | 6 | 0.65747 | 0.99752 | 0.78387 | 0.60884 | 0.54398